FALCON FIRE PROTECTION DISTRICT

Fire Prevention Division

7030 Old Meridian Road

Falcon, Colorado 80831

Business Number: 719-495-4050     Business Fax: 719-495-3112

Lieutenant/Fire Inspector II           Curtis L. Kauffman

Email: ckauffman@falconfirepd.org                     Cell #: 719-641-2139

Date: December 03, 2025

To: EDARP

C/O: Maria Lancto

Planning & Community Development

2882 International Circle, Suite 110

Colorado Springs, CO 80910

Phone: 719-520-6447

Email: MariaLancto@elpasoco.com

Project Name: 10890 Salbeck Lane-Size of Accessory Structure in RR-5

File Prefix: BOA-Board of Adjustment

Parcel/s: 5223004001

Zone: RR-5

File Number: BOA255

This letter serves as comments for the adjustment. You are responsible for complying with all section’s, codes and references with the fire code based on the 2021 International Fire Code.

PLEASE READ THIS ENTIRE DOCUMENT, YOU ARE RESPONSIBLE FOR EVERYTHING CONTAINED HERIN!

The following are ACTION ITEMS that need to be completed prior to the fire final.

503.1.1 Buildings and facilities. Approved fire apparatus access roads shall be provided for

every facility, building or portion of a building hereafter constructed or moved into or within the jurisdiction. The fire apparatus access road shall comply with the requirements of this section and shall extend to within 150 feet (45 720 mm) of all portions of the facility and all portions of the exterior walls of the first story of the building as measured by an approved route around the exterior of the building or facility.

Exceptions:

1. The fire code official is authorized to increase the dimension of 150 feet (45 720

mm) where any of the following conditions occur:

1.1. The building is equipped throughout with an approved automatic sprinkler

system installed in accordance with Section 903.3.1.1, 903.3.1.2 or 903.3.1.3.

1.2. Fire apparatus access roads cannot be installed because of location on

property, topography, waterways, nonnegotiable grades or other similar

conditions, and an approved alternative means of fire protection is provided.

1.3. There are not more than two Group R-3 or Group U occupancies.

2. Where approved by the fire code official, fire apparatus access roads shall be

permitted to be exempted or modified for solar photovoltaic power generation

facilities.

503.2 Specifications. Fire apparatus access roads shall be installed and arranged in accordance with Sections 503.2.1 through 503.2.8 and Appendix D.

503.2.1 Dimensions. Fire apparatus access roads shall have an unobstructed width of not less than 20 feet (6096 mm), exclusive of shoulders, except for approved security gates in accordance with Section 503.6, and an unobstructed vertical clearance of not less than 13 feet 6 inches (4115 mm). modifications to the required access widths where they are inadequate for fire or rescue operations or where necessary to meet the public safety objectives of the jurisdiction.

503.2.2 Authority. The fire code official shall have the authority to require or permit modifications to the required access widths where they are inadequate for fire or rescue operations or where necessary to meet the public safety objectives of the jurisdiction.

Section 503.2.3 Surface. Fire apparatus access roads shall be designed and maintained to support the imposed loads of fire apparatus and shall be surfaced so as to provide all-weather driving capabilities.

503.2.4 Turning radius. The required turning radius of a fire apparatus access road shall be determined by the fire code official.  33’ inside and 53’ outside radius. Resubmit the site plan showing the turning radius.

503.2.5 Dead ends. Dead-end fire apparatus access roads in excess of 200 feet in length shall be provided with an approved area for turning around fire apparatus.

503.2.7 Grade. The grade of the fire apparatus access road shall be within the limits established by the fire code official based on the fire department’s apparatus. 10% maximum.

503.2.8 Angles of approach and departure. The angles of approach and departure for fire apparatus access roads shall be within the limits established by the fire code official based on the fire department’s apparatus. Less than 8° degrees (not % percent).

503.3 Marking. Where required by the fire code official, approved signs or other approved

notices or markings that include the words “NO PARKING—FIRE LANE” shall be provided for fire apparatus access roads to identify such roads or prohibit the obstruction thereof. The means by which fire lanes are designated shall be maintained in a clean and legible condition at all times and be replaced or repaired when necessary to provide adequate visibility.

503.4 Obstruction of fire apparatus access roads. Fire apparatus access roads shall not be

obstructed in any manner, including the parking of vehicles. The minimum widths and clearances established in Sections 503.2.1 and 503.2.2 shall be maintained at all times

503.6 Security gates. The installation of security gates across a fire apparatus access road shall be approved by the fire code official. Where security gates are installed, they shall have an approved means of emergency operation. The security gates and the emergency operation shall be maintained operational at all times. Electric gate operators, where provided, shall be listed in accordance with UL 325. Gates intended for automatic operation shall be designed, constructed and installed to comply with the requirements of ASTM F2200. This only applies if installing a gate across the driveway.

Section 505.1. Address Identification. New and existing buildings shall have approved address numbers, building numbers or approved building identification placed in a position that is plainly legible and visible from the street or road fronting the property. These numbers shall contrast with their background. Address numbers shall be Arabic numbers or alphabetical letters. Numbers shall be a minimum of five (5) inches (127 mm) high with a minimum stroke width of one half (0.5) inch (12.7 mm). Where access is by means of a private road and the building cannot be viewed from the public way, a monument, pole or other means of signage shall be used to identify the structure.” Address numbers shall be visible from the street side and in both directions of road travel.

Section D102.1 Access and loading. Facilities, buildings, or portions of buildings hereafter constructed shall be accessible to fire department apparatus by way of an approved fire apparatus access road with asphalt, concrete, or other approved driving surface capable of supporting the imposed load of fire apparatus weighing up to 75,000 pounds with a minimum single axle weight of 27,000 pounds.

D105.1 Where required. Where the vertical distance between the grade plane and the highest roof surface exceeds 30 feet (9144 mm), approved aerial fire apparatus access roads shall be provided. For purposes of this section, the highest roof surface shall be determined by measurement to the eave of a pitched roof, the intersection of the roof to the exterior wall, or the top of parapet walls, whichever is greater.

Exception: Where approved by the fire code official, buildings of Type IA, Type IB or Type IIA construction equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 and having fire fighter access through an enclosed stairway with a Class I standpipe from the lowest level of fire department vehicle access to all roof surfaces.

D105.2 Width. Aerial fire apparatus access roads shall have a minimum unobstructed width of 26 feet (7925 mm), exclusive of shoulders, in the immediate vicinity of the building or portion thereof.

The following are ATTENTION ITEMS that apply to this review.

Section 1402.1 Temporary Fire Access Road. Temporary access roads shall be an all-weather surface comprised of either the first lift of asphalt or concrete/compacted gravel to a thickness capable of supporting the imposed loads of fire department apparatus. A 20-foot minimum width shall be maintained unless the permanent road is designed less than 20 feet, in which case the temporary road shall be the intended width of the permanent road. Adequate street signs and fire lane signs shall be installed where applicable. Temporary access roads must be maintained in accordance with this section. Temporary roads serving as fire lanes shall not be in place more than 6 months without special approval from the fire department.”

TIMING OF INSTALLATION: Fire department access roads shall be made serviceable prior to and during the time of construction except when approved alternative methods of protection are provided.

ACCESS FOR FIREFIGHTING: Approved vehicle access for firefighting shall be provided to all construction/demolition sites. Vehicle access shall be provided by either temporary or permanent roads capable of supporting vehicle loading under all weather conditions. Vehicle access shall be maintained until permanent fire apparatus access roads are available.

Attention Contractor/Applicant:

YOU ARE RESPONSIBLE TO COMPLETE THE FOLLOWING ITEMS.

Please complete the following items:

- Permits – Insure all applicable permits are obtained from the Pikes Peak Regional Building Department (PPRBD).

- Follow the Colorado State Forest Service for all mitigation guidelines and the new Colorado Wildfire Resiliency Code as of July 01, 2026.

- Review the comment letter from Falcon Fire Protection District. You are responsible for complying with the entire fire code as amended and any applicable NFPA’s referenced.

- Ensure all Action Items have been addressed.

- Plan review comments (this letter) shall be on site and available to the fire inspector.

- A new site plan shall show the turning radii on the existing driveway. The new site plan shall be submitted to Falcon Fire Protection District for approval.

Please let me know if there are any questions and/or concerns. You may contact me via the email at the top of the letter.

Sincerely,

Curtis L. Kauffman

Curtis L. Kauffman

Fire Prevention Division

Lieutenant/Fire Inspector II