FALCON FIRE PROTECTION DISTRICT

Fire Prevention Division

7030 Old Meridian Road

Falcon, Colorado 80831

Business Number: 719-495-4050     Business Fax: 719-495-3112

Lieutenant/Fire Marshal           	    Curtis L. Kauffman

Email: ckauffman@falconfirepd.org                    Cell #: 719-641-2139

Date: September 9, 2026

To: EDARP

C/O: Maranda Benson

Planning & Community Development

2882 International Circle, Suite 110

Colorado Springs, CO 80910

Phone: 719-520-7940

Email: mirandabenson2@elpasoco.com

Project Name: 12555 Garrett Road Rural Home Occupation

File Prefix: AL-Special Use

Parcel/s: 4319001033

Zone: RR-5

File Number: AL2619

Review #: 1

This letter serves as plan review comments. You are responsible for complying with all sections, codes and references with the fire code based on the 2021 International Fire Code and local amendments.

Amendments in RED.

Comments in BLUE.

PLEASE READ THIS ENTIRE DOCUMENT, YOU ARE RESPONSIBLE FOR EVERYTHING CONTAINED HERIN!

The following are ACTION ITEMS that need to be completed prior to the fire final.

101.3 Purpose. The purpose of this code is to establish the minimum requirements consistent with nationally recognized good practice for providing a reasonable level of life safety and property protection from the hazards of fire, explosion or dangerous conditions in new and existing buildings, structures and premises, and to provide a reasonable level of safety to fire fighters and emergency responders during emergency operations.

102.7 Referenced codes and standards. The codes and standards referenced in this code shall be those that are listed in Chapter 80, and such codes and standards shall be considered to be part of the requirements of this code to the prescribed extent of each such reference and as further regulated by Sections 102.7.1 and 102.7.2.

102.7.1 Conflicts. Where conflicts occur between provisions of this code and referenced codes and standards, the provisions of this code shall apply.

102.7.2 Provisions in referenced codes and standards. Where the extent of the

reference to a referenced code or standard includes subject matter that is within the scope of this code, the provisions of this code, as applicable, shall take precedence over the provisions in the referenced code or standard.

105.1.1 Permits required. A property owner or owner’s authorized agent who intends to conduct an operation or business, or install or modify systems and equipment that are regulated by this code, or to cause any such work to be performed, shall first make application to the fire code official and obtain the required permit.

- Major concern, the access to the landscaping shop and outdoor storage is using the address of 12555 Garrett Road. Using this address and access, there is no access to the shop and outdoor storage due to the creek behind the home. I do see that there is access to the shop and outdoor storage using Richardson Lane. This is very confusing for responding emergency personnel. Please add an address for the shop and outdoor storage with Richardson Lane numbers. Using the Garrett Road address will increase the reasons time during an emergency.

- The driveway leading to the shop and outdoor storage shall support fire apparatus weighting 75,000 pounds plus.

- Make sure that the fire department can turn-around an aerial ladder vehicle.

- Are any chemicals stored on site?

- If there is a locked gate for the entrance from Richardson Lane, a Knox padlock shall be purchased, contact the Falcon Fire Protection District Fire Marshal for model.

Attention Contractor/Applicant:

YOU ARE RESPONSIBLE TO COMPLETE THE FOLLOWING ITEMS.

Please complete the following items:

- Follow the Colorado State Forest Service for all mitigation guidelines for all future planting of materials. Low-Flammability Landscape Plants and Ignition-Resistant Landscape plants.

- Review of the comment letter from Falcon Fire Protection District. You are responsible for complying with the entire fire code, local amendments and any applicable NFPA’s referenced.

- Ensure all Action Items have been addressed.

Please let me know if there are any questions and/or concerns. You may contact me via the email at the top of the letter.

Sincerely,

Curtis L. Kauffman

Curtis L. Kauffman

Fire Prevention Division

Lieutenant/Fire Marshal