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Fire Prevention Division
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Falcon, Colorado 80831
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        Lieutenant/Fire Marshal                 Curtis L. Kauffman
           Email: ckauffman@falconfirepd.org                     Cell #: 719-641-2139


Date: August 10, 2026

To: EDARP		
C/O: Maranda Benson
Planning & Community Development
2882 International Circle, Suite 110
Colorado Springs, CO 80910
Phone: 719-520-7940
Email: mirandabenson2@elpasoco.com


Project Name: Willow Springs Estates Filing No. 2
File Prefix: VR-Vacation and Replat
Parcel/s: 5115003006
Zone: RR-5
File Number: VR2664
Review #: 1


This letter serves as the third plan review comments. You are responsible for complying with all sections, codes and references with the fire code based on the 2021 International Fire Code, local amendments, and NFPA standards. 

RED: Local Amendments
BLUE: Fire District Comments

1) Falcon Fire Protection District fire station #1 (12072 Royal County Down Road) is 12.5 miles from this address. Black Forest Fire Rescue fire station #2 16465 Ridge Run Drive) is 4.86 miles from this address. Monument Fire District fire station #2 (18460 Roller Coaster Road) is 8.41 miles from this address. Both Black Forest Fire Rescue and Monument Fire District are automatic in response with Falcon Fire Protection District on all reported fires (structures and wildland). 

2) There is no central water supply in this area. All water supply must be trucked using water tenders from the local and mutual-aid fire departments. Falcon Fire Protection District water tenders carry 2,000-gallons each (x4), mutual-aid water tenders carry 2,000-gallons each or more.

3) Water supply cistern locations: Bison Meadows is 4.56 miles and Black Forest Fire Rescue fire station #2 is 4.86 miles from this address. Both cisterns hold 30,000-gallons each. There are two more citterns within seven miles of this address at 30,000-gallons each. 


4) With Black Forest Fire Rescue fire station #2 within 5 road miles, this address is an ISO Class 3. 

5) Follow the El Paso County Planning & Community Development (PCD) Land Development Code (LDC) for driveway specifications. 

6) Minium driveway width and height; 12-feet wide and 13-feet 6-inches in height shall always be maintained. 
a. D102.1 Access and loading. Facilities, buildings, or portions of buildings hereafter constructed shall be accessible to fire department apparatus by way of an approved fire apparatus access road with asphalt, concrete, or other approved driving surface capable of supporting the imposed load of fire apparatus weighing up to 75,000 pounds with a minimum single axle weight of 27,000 pounds. Alternative methods such as brick pavers, road, base, and gravel as approved by the fire code official. 
b. 503.2.4 Turning radius. The required turning radius of a fire apparatus access road shall be determined by the fire code official. 33’ inside and 53’ outside radius. Resubmit the site plan showing the turning radius.

7) Address: 505.1 Address identification. New and existing buildings shall be provided with approved address identification. The address identification shall be legible and placed in a position that is visible from the street or road fronting the property. Address identification characters shall contrast with their background. Address numbers shall be Arabic numbers or alphabetical letters. Numbers shall not be spelled out. Each character shall be not less than 4 (four) inches (102 mm) high with a minimum stroke width of 1/2 inch (12.7 mm). Address size based on distance from the street: up to 75 feet is 5 inches, greater than 75 to 150 feet is 6 inches; greater than 150 feet to 250 feet is 8 inches; and greater than 250 feet is 10 inches 5 inches high with a minimum stroke width of 1/2 inch. Where required by the fire code official, address identification shall be provided in additional approved locations to facilitate emergency response. Where access is by means of a private road and the building cannot be viewed from the public way, a monument, pole, or other sign or means shall be used to identify the structure. Address identification shall be maintained. Address numbers at the end of the driveway are visible from both directions of travel on Quarterhorse Lane and on the building. 

8) Follow the Colorado State Forest Service for all mitigation guidelines. 



Please let me know if there are any questions and/or concerns. You may contact me via email at the top of the letter. 


Sincerely,

Curtis L. Kauffman

Curtis L. Kauffman
Fire Prevention Division
Lieutenant/Fire Marshal 
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