FALCON FIRE PROTECTION DISTRICT

Fire Prevention Division

7030 Old Meridian Road

Falcon, Colorado 80831

Business Number: 719-495-4050     Business Fax: 719-495-3112

Lieutenant/Fire Marshal                 Curtis L. Kauffman

Email: ckauffman@falconfirepd.org                     Cell #: 719-641-2139

Date: August 10, 2026

To: EDARP

C/O: Maranda Benson

Planning & Community Development

2882 International Circle, Suite 110

Colorado Springs, CO 80910

Phone: 719-520-7940

Email: mirandabenson2@elpasoco.com

Project Name: 11185 Eggar Drive Falcon Baptist Church Addition

File Prefix: PPR-Plot Plan Review

Parcel/s: 5313002016

Zone: RR-5

File Number: PPR2516

Review #: 3

This letter serves as the third plan review comments. You are responsible for complying with all sections, codes and references with the fire code based on the 2021 International Fire Code, local amendments, and NFPA standards.

- The new plot plan does not show a fire apparatus access road to the fire pump house or to the onsite cisterns. A fire apparatus access road shall be provided.

- The existing fire alarm system and existing fire sprinkler system shall be extended into the addition. Submit updated cut sheets for both systems.

- The existing Knox Box shall be moved to the west elevation, to the right of the double doors. Top of the Knox Box shall be 5 feet up from the sidewalk.

- The development/access plan review fees shall be paid in full before further plan reviews are submitted.

DEVELOPMENT/ACCESS PLAN REVIEW FEES:

The Falcon Fire Department collects a cost recovery fee of $429.00 for development plan reviews.

Please let me know if there are any questions and/or concerns. You may contact me via email at the top of the letter.

Sincerely,

Curtis L. Kauffman

Curtis L. Kauffman

Fire Prevention Division

Lieutenant/Fire Marshal