FALCON FIRE PROTECTION DISTRICT

Fire Prevention Division

7030 Old Meridian Road

Falcon, Colorado 80831

Business Number: 719-495-4050     Business Fax: 719-495-3112

Lieutenant/Fire Inspector II           Curtis L. Kauffman

Email: ckauffman@falconfirepd.org                     Cell #: 719-641-2139

Date: September 29, 2025

To: EDARP

C/O: Lacey Dean

Planning & Community Development

2882 International Circle, Suite 110

Colorado Springs, CO 80910

Phone: 719-520-7943

Email: LaceyDean2@elpasoco.com

Project Name: Utah-Nevada Lane-RV and Self-Storage

File Prefix: PPR-Plot Plan Review

Parcel/s: 5308000002, 5308000071, 5308000082

Current Zoning: RR-5

File Number: PPR2526

This letter serves as plan review comments. You are responsible for complying with all section’s, codes and references with the fire code based on the 2021 International Fire Code.

PLEASE READ THIS ENTIRE DOCUMENT, YOU ARE RESPONSIBLE FOR EVERYTHING CONTAINED HERIN!

The following are ACTION ITEMS that need to be completed prior to the fire final.

312.1 General. Vehicle impact protection required by this code shall be provided by posts that comply with Section 312.2 or by other approved physical barriers that comply with Section 312.3.

312.2 Posts. Guard posts shall comply with all of the following requirements:

1. Constructed of steel not less than 4 inches (102 mm) in diameter and concrete filled.

2. Spaced not more than 4 feet (1219 mm) between posts on center.

3. Set not less than 3 feet (914 mm) deep in a concrete footing of not less than a 15-inch (381

mm) diameter.

4. Set with the top of the posts not less than 3 feet (914 mm) above ground.

5. Located not less than 3 feet (914 mm) from the protected object.

312.3 Other barriers. Barriers, other than posts specified in Section 312.2, that are designed to resist, deflect or visually deter vehicular impact commensurate with an anticipated impact scenario shall be permitted where approved.

Section 505.1. Address Identification. New and existing buildings shall have approved address numbers, building numbers or approved building identification placed in a position that is plainly legible and visible from the street or road fronting the property. These numbers shall contrast with their background. Address numbers shall be Arabic numbers or alphabetical letters. Numbers shall be a minimum of five (5) inches (127 mm) high with a minimum stroke width of one half (0.5) inch (12.7 mm). Where access is by means of a private road and the building cannot be viewed from the public way, a monument, pole or other means of signage shall be used to identify the structure.”

505.2 Street or road signs. Streets and roads shall be identified with approved signs. Temporary

signs shall be installed at each street intersection when construction of new roadways allows passage by vehicles. Signs shall be of an approved size, weather resistant and be maintained until replaced by permanent signs.

503.1 Where required. Fire apparatus access roads shall be provided and maintained in

accordance with Sections 503.1.1 through 503.1.3 and Appendix D.

503.1.1 Buildings and facilities. Approved fire apparatus access roads shall be provided for every facility, building or portion of a building hereafter constructed or moved into or within the jurisdiction. The fire apparatus access road shall comply with the requirements of this section and shall extend to within 150 feet (45 720 mm) of all portions of the facility and all portions of the exterior walls of the first story of the building as measured by an approved route around the exterior of the building or facility.

Exceptions:

1. The fire code official is authorized to increase the dimension of 150 feet (45 720

mm) where any of the following conditions occur:

1.1. The building is equipped throughout with an approved automatic sprinkler

system installed in accordance with Section 903.3.1.1, 903.3.1.2 or 903.3.1.3.

1.2. Fire apparatus access roads cannot be installed because of location on

property, topography, waterways, nonnegotiable grades or other similar

conditions, and an approved alternative means of fire protection is provided.

1.3. There are not more than two Group R-3 or Group U occupancies.

2. Where approved by the fire code official, fire apparatus access roads shall be

permitted to be exempted or modified for solar photovoltaic power generation

facilities.

503.2 Specifications. Fire apparatus access roads shall be installed and arranged in accordance with Sections 503.2.1 through 503.2.8 and Appendix D.

503.2.1 Dimensions. Fire apparatus access roads shall have an unobstructed width of not less than 20 feet (6096 mm), exclusive of shoulders, except for approved security gates in accordance with Section 503.6, and an unobstructed vertical clearance of not less than 13 feet 6 inches (4115 mm). modifications to the required access widths where they are inadequate for fire or rescue operations or where necessary to meet the public safety objectives of the jurisdiction.

503.2.2 Authority. The fire code official shall have the authority to require or permit

Section 503.2.3 Surface. Fire apparatus access roads shall be designed and maintained to support the imposed loads of fire apparatus and shall be surfaced so as to provide all-weather driving capabilities.

503.2.4 Turning radius. The required turning radius of a fire apparatus access road shall be determined by the fire code official.  33’ inside and 53’ outside radius.

503.2.5 Dead ends. Dead-end fire apparatus access roads in excess of 200 feet in length shall be provided with an approved area for turning around fire apparatus.

Section 503.3 Marking. Where required by the fire code official, approved signs or other approved notices or markings that include the words “NO PARKING—FIRE LANE” shall be provided for fire apparatus access roads to identify such roads or prohibit the obstruction thereof. The means by which fire lanes are designated shall be maintained in a clean and legible condition at all times and be replaced or repaired when necessary to provide adequate visibility.  Preferably metal signs so the winter snow does not cover this wording.

Section 503.4 Obstruction of fire apparatus access roads. Fire apparatus access roads shall not be obstructed in any manner, including the parking of vehicles. The minimum widths and clearances established in Sections 503.2.1 and 503.2.2 shall be maintained at all times.

503.6 Security gates. The installation of security gates across a fire apparatus access road shall be approved by the fire code official. Where security gates are installed, they shall have an approved means of emergency operation. The security gates and the emergency operation shall be maintained operational at all times. Electric gate operators, where provided, shall be listed in accordance with UL 325. Gates intended for automatic operation shall be designed, constructed and installed to comply with the requirements of ASTM F2200. Diablo Vehicle Detection and Gate Opening System for both gates. Two Knox Gate & Key Switch, one for each vehicle gate as a backup to the Diablo system. Model KLS-3502.

506.1 Where required. Where access to or within a structure or an area is restricted because of secured openings or where immediate access is necessary for lifesaving, or fire-fighting purposes, or where monitored fire protection systems or elevators exist in the building, the fire code official is authorized to require a key box to be installed in an approved location. The key box shall be of an approved type listed in accordance with UL 1037 and shall contain keys to gain necessary access as required by the fire code official.  Order one Knox Box KLS-3200. Model KLS-3271.

507.1 Required water supply. An approved water supply capable of supplying the required fire flow for fire protection shall be provided to premises on which facilities, buildings or portions of buildings are hereafter constructed or moved into or within the jurisdiction.  30,000-gallon water cistern as discussed during our meetings. Contact me for a final meeting prior to ordering the cistern.

507.5.6 Physical protection. Where fire hydrants are subject to impact by a motor vehicle, guard posts or other approved means shall comply with Section 312.

Section D102.1 Access and loading. Facilities, buildings, or portions of buildings hereafter constructed shall be accessible to fire department apparatus by way of an approved fire apparatus access road with asphalt, concrete, or other approved driving surface capable of supporting the imposed load of fire apparatus weighing up to 75,000 pounds with a minimum single axle weight of 27,000 pounds.

D103.5 Fire apparatus access road gates. Gates securing the fire apparatus access roads shall comply with all of the following criteria:

1. Where a single gate is provided, the gate clear opening width shall be not less than 16 feet or as approved by the fire code official. Where a fire apparatus road consists of a divided roadway, the gate clear opening width shall be not less than 16 feet or as approved by the fire code official.

2. Gates shall be approved by the fire code official.

3. Construction of gates shall be of materials that allow manual operation by one person.

4. Gate components shall be maintained in an operative condition at all times and replaced or repaired when defective.

5. Electric gates shall be equipped with a means of opening the gate by fire department personnel for emergency access. When outbound/egress movements do not include an automatic method of the gate opening when a vehicle is present, an approved means of opening the gate by the fire department shall be provided. Emergency opening devices shall be approved by the fire code official.

6. Methods of locking shall be submitted for approval by the fire code official.

7. Electric gate operators, where provided, shall be listed in accordance with UL 325.

8. Gates intended for automatic operation shall be designed, constructed, and installed to comply with the requirements of ASTM F2200.

D105.1 Where required. Where the vertical distance between the grade plane and the highest roof surface exceeds 30 feet (9144 mm), approved aerial fire apparatus access roads shall be provided. For purposes of this section, the highest roof surface shall be determined by measurement to the eave of a pitched roof, the intersection of the roof to the exterior wall, or the top of parapet walls, whichever is greater.

Exception: Where approved by the fire code official, buildings of Type IA, Type IB or Type

IIA construction equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 and having fire fighter access through an enclosed stairway with a Class I standpipe from the lowest level of fire department vehicle access to all roof surfaces.

D105.2 Width. Aerial fire apparatus access roads shall have a minimum unobstructed width of 26 feet (7925 mm), exclusive of shoulders, in the immediate vicinity of the building or portion thereof.

D105.3 Proximity to building. One or more of the required access routes meeting this condition shall be located not less than 15 feet (4572 mm) and not greater than 30 feet (9144 mm) from the building, and shall be positioned parallel to one entire side of the building. The side of the building on which the aerial fire apparatus access road is positioned shall be approved by the fire code official.

D105.4 Obstructions. Overhead utility and power lines shall not be located over the aerial fire apparatus access road or between the aerial fire apparatus road and the building. Other obstructions shall be permitted to be placed with the approval of the fire code official.

The following are ATTENTION ITEMS that apply to this review.

Section 1402.1 Temporary Fire Access Road. Temporary access roads shall be an all-weather surface comprised of either the first lift of asphalt or concrete/compacted gravel to a thickness capable of supporting the imposed loads of fire department apparatus. A 20-foot minimum width shall be maintained unless the permanent road is designed less than 20 feet, in which case the temporary road shall be the intended width of the permanent road. Adequate street signs and fire lane signs shall be installed where applicable. Temporary access roads must be maintained in accordance with this section. Temporary roads serving as fire lanes shall not be in place more than 6 months without special approval from the fire department.”

TIMING OF INSTALLATION: Fire department access roads shall be made serviceable prior to and during the time of construction except when approved alternative methods of protection are provided.

ACCESS FOR FIREFIGHTING: Approved vehicle access for firefighting shall be provided to all construction/demolition sites. Vehicle access shall be provided by either temporary or permanent roads capable of supporting vehicle loading under all weather conditions. Vehicle access shall be maintained until permanent fire apparatus access roads are available.

Attention Contractor/Applicant:

YOU ARE RESPONSIBLE TO COMPLETE THE FOLLOWING ITEMS.

Please complete the following items:

- Permits – Insure all applicable permits are obtained from the Pikes Peak Regional Building Department (PPRBD) and the Colorado Springs Fire Department construction services.

- All new building plans shall be submitted to the Falcon Fire Protection District and the Colorado Springs Fire Department Construction Services (building, fire alarm system, fire sprinkler system, and Hazardous material etc.) for review. All correspondence with PPRBD and Construction Services of Colorado Springs Fire Department shall include the email above.

- Follow the 2021 edition of the International Fire Code (IFC), chapter 33-Fire Safety During Construction and Demolition shall be adhered to at all times. The contractor shall provide this information to Falcon Fire Protection District-Fire Prevention Division

- Follow the Colorado State Forest Service for all mitigation guidelines.

- Review the comment letter from Falcon Fire Protection District. You are responsible for complying with the entire fire code as amended and any applicable NFPA’s referenced.

- Ensure all Action Items have been addressed.

- Plan review comments (this letter) shall be on site and available to the fire inspector.

Please let me know if there are any questions and/or concerns. You may contact me via the email at the top of the letter.

Sincerely,

Curtis L. Kauffman

Curtis L. Kauffman

Fire Prevention Division

Lieutenant/Fire Inspector II