Responses to Comments

Detention Maintenance Agreement

- The property owner identified on the Assessor’s website is not that identified in the DMA agreement. Please correct this. I will sign the updated agreement after it is confirmed correct party is identified and has signed the agreement. Thanks. Property owner information has been updated.

Drainage Letter

- State the current % of native and level of imperviousness. Statement added to report text

- Because the site is infiltrating storms greater than the WQCV please provide proof of approval from the state that the project site has the water rights to do so. The project alters historic patterns, please discuss. Discussion added to report text.

- State the existing and proposed % and ensure the actual conditions are accounted for in the drainage calcs. There is much more area being used for storage then is reflected on the SDP and GEC. With this storage and the new concrete parking and new millings area the level of imperviousness for the site is greater than 30%. Existing and proposed % impervious updated throughout report.

- Only runoff exceeding the 100-year storm event will be leaving the site. That is different from historic. Text updated.

- This value is low for the current and proposed conditions. All the outdoor storage with dumpsters, vehicles, and added concrete and new millings needs to be included. There are also areas that are not properly stabilized that need ground cover which will increase the impervious %. Impervious percent updated.

- Unresolved: Please submit the SDI form as a separate slot as well in EDARP. Noted.

- Provide the full SDI sheets not just the results so it is clear what was assumed in the calculations. Unsure what is intended by this comment.

- Update FDR map to reflect actual conditions. See comments on the SDP and GEC. Map updated.

GEC Checklist

- Earth disturbances shall be conducted in such a manner so as to effectively minimize accelerated soil erosion and resulting sedimentation. All disturbances shall be designed, constructed, and completed so that the exposed area of any disturbed land shall be limited to the shortest practical period of time. Pre-existing vegetation shall be protected and maintained within 50 horizontal feet of receiving water unless shown to be infeasible and specifically requested and approved. In addition to maintaining 50 horizontal feet of pre-existing vegetation upgradient of a receiving water (unless infeasible and approved), the Permit Holder(s) must install CCMs upgradient of the vegetative buffer. GEC plans updated to meet this checklist criteria.

GEC Plans

- Replace with GEC checklist standard note 7. Note updated.

- Where are these shown on the grading plan? Existing asphalt millings are the lighter shaded areas in the parking lot and proposed concrete is for the accessible stalls.

- All these drive area surfaces will need to be stabilized and covered. There are large areas on the GEC that do not show a surface type that are bare dirt. With this heavy truck traffic it will erode. Areas updated to be stabilized with gravel.

- Provide bottom width, foreslope, and min. depth of this swale created by the proposed berm. Swale details added to berm detail.

- This area is not stabilized with existing millings. It is onsite, but doesn’t show up in aerials or on Google Earth. It is planned to be top dressed with new asphalt millings and has been accounted for in the sand filter basin sizing.

- See previous comments on the sheet above. Label what surface the areas outside the limits of disturbance will be. Not 3 added to top of sheet G.3 addressing areas outside of limits of disturbance.

- Provide length of level spreader. Will the slopes at each of the notches need erosion protection/riprap rundowns? We see erosion along the slopes of PLDs and SFBs oftentimes in the field. Length and riprap added.

- Show sand filter media in cross sections. Added.

- How long is the level spreader? Clarify in plan view. Dimension added in plan view.

TIS

- Update Road Impact Fee section. Section updated.