Project: Gateway Trucking – Variance of Use Permit

Code: 2021 IFC

- Change of Use/ Expansion – The proposed expansion of the truck equipment yard and storage area exceeds scope of prior approval (VA-15-004) and requires full fire code review. Clearly delineate all proposed operational, storage, parking, and circulation areas on the site plan. (IFC 102.1, 105.3.1)

- Fire Apparatus Access – Provide approved apparatus access to all access to all areas of equipment storage and operation. Access roads shall maintain a minimum of 20-foot unobstructed width, 13’6” vertical clearance, and an all – weather surface capable of supporting fire apparatus. (IFC 503; Appendix D)

- Dead – End Access/ Turning Radius – Identify all dead- end fire apparatus access roads and provide compliant turnaround geometry where required. (IFC Appendix D)

- Water Supply for Fire Protection – Water supply requirements will need to be met in form of a hydrant or cistern (NFPA 1142)

- Outdoor Storage Configuration- Outdoor storage of vehicles and equipment shall maintain required fire apparatus access, separation distances, and emergency access lanes. Storage shall not obstruct access roads or fire lanes. (IFC 315)

- Hazardous Materials- Storage of fuel, oils, lubricants, batteries, compressed gases, or other hazardous materials is not approved unless specifically identified and reviewed. Provide confirmation or submit a hazardous materials inventory statement if applicable (IFC Chapters 50-67)

- Address Identification- Provide approved address identification for each parcel, visible from the responding roadway and compliant with IFC size, contrast, and placement requirements. (IFC 505)

- Vegetation Management- Maintain vegetation clearance to ensure fire apparatus access and reduce fire spread potential throughout the site. (IFC 304)

- Operational Limitations – Approval of this variance does not authorize future expansion, increased storage density, fuel storage, utilities, or structures without additional fire code review and approval. (IFC 104.1, 104.7)