EPC Pond Comments:

EPC DPW Stormwater

Review 1: EPC DPW Stormwater comments have been provided (in orange text boxes) on the following uploaded documents: - CDs - Drainage Report - ESQCP - FAE - GEC Checklist - PCM Applicability Form - PCM Maintenance Agreement - PCM - MHFD Detention Calcs or SDI Form - PCM O&M Manual - SWMP - SWMP Checklist Please provide the following document upon resubmittal: - PCM - Notice of Intent to Construct a Non-Jurisdictional Water Impoundment Structure (proof of submittal) Reviewed by: Mikayla Hartford, P.E. Engineer - Stormwater 719.339.5053 MikaylaHartford@elpasoco.com Zachary Jannusch Associate Engineer - Stormwater 719.500.3170 ZacharyJannusch@elpasoco.com
[image: ]

M&S RESPONSE: The Non-Jurisdictional Water Structure Notice for 3 ponds have been completed and sent to the DWR. Please find the attached poof of submittal.

_________________________________________________________________________
EPC DPW Development Services - Engineering

Engineering Review Ver.1 Please see engineer review comments on the following documents FDR_V1 CD_V1s FAE_V1 ESQCP_V1 Provide Detention Maintenance Agreement GEC_V1 Note the CDs and GEC plan set can be combined into one set since they are same sheets. Edward Schoenheit, Engineer E.P.C. Dept. of Public Works 2880 International Circle Colorado Springs, CO. 80910 Office: 719.520.6813 Cell: 719.502.9659 edwardschoenheit@elpasoco.com https://publicworks.elpasoco.com/department-public-works/county-engineer/
M&S RESPONSE: Storm, PCM and GEC plans are all combined into one 27 plan package
image1.png
Proof of Submittal of the Colorado Division of Water Resources (DWR) “Notice of Intent to Construct a
Non-Jurisdictional Water Impoundment Structure.” Any Applicant proposing to construct a reservoir for
the purpose of storing water, (i.., water quality and/or detention facility), shall submit notice thereof to
the State Engineer prior to the beginning of any construction. Such notice shallinclude the location of such
proposed reservoir with reference to Section, Township, and Range and the dimensions of the reservoir,
the dam, and the spillway. If any reservoir is constructed without the notice required, the State Engineer
‘may prohibit the storage of water i such reservoir or direct the withdrawal of water from such reservoir.
This notice is required per CRS 37-87-125 and must be submitted to the Colorado Division of Water
Resources (DWR) Dam Safety Engineer's Office a Jm of 45 days prior to construction. Proof of this
notice i required to be submitted to the County.

Jurisdictional Size Dam, A dam creating a reservoir with a capacity of more than one hundred (100) acre-
feet, ora surface area in excess of twenty (20) acres at the high waterline, or where the jurisdictional height
exceeds ten (10) feet.

Non-Jurisdictional Size Dam. A dam creating a reservoir with a capacity of one hundred (100) acre-feet or
less, and a surface area of twenty (20) acres or less, and a jurisdictional height of ten (10) feet or less. Non-
jurisdictional size dams are regulated and subject to the authority of the State Engineer.

Additional information regarding the Rules and Regulations for Dam Safety and Dam Construction i
available on the State of Colorado Division of Water Resources website (see Section 1.8.2).





