FALCON FIRE PROTECTION DISTRICT

Fire Prevention Division

7030 Old Meridian Road

Falcon, Colorado 80831

Business Number: 719-495-4050     Business Fax: 719-495-3112

Lieutenant/Fire Marshal                 Curtis L. Kauffman

Email: ckauffman@falconfirepd.org                     Cell #: 719-641-2139

Date: February 27, 2026

To: EDARP

C/O: Lisa Elgin

Planning & Community Development

2882 International Circle, Suite 110

Colorado Springs, CO 80910

Phone Number: 719-520-6449

Email: LisaElgin@elpasoco.com

Project Name: 4490 E. Blaney Road Tower Modification

File Prefix: TWR-Tower

Parcel/s: 4330000001

File Number: TWR262

Comments:

- Address numbers shall be placed on the building (southeast corner just below the roof line) and by the driveway leading from the main driveway to the home to the Verizon building with an arrow.

Section 505.1. Address Identification. New and existing buildings shall have approved address numbers, building numbers or approved building identification placed in a position that is plainly legible and visible from the street or road fronting the property. These numbers shall contrast with their background. Address numbers shall be Arabic numbers or alphabetical letters. Numbers shall be a minimum of five (5) inches (127 mm) high with a minimum stroke width of one half (0.5) inch (12.7 mm). Where access is by means of a private road and the building cannot be viewed from the public way, a monument, pole or other means of signage shall be used to identify the structure.”

- One Knox Box shall be mounted onto the building, right side of the man door. The top of the Knox Box shall be five-feet up from the ground. One Knox padlock shall be placed on the chain for the gate.

506.1 Where required. Where access to or within a structure or an area is restricted because of secured openings or where immediate access is necessary for lifesaving, or fire-fighting purposes, or where monitored fire protection systems or elevators exist in the building, the fire code official is authorized to require a key box to be installed in an approved location. The key box shall be of an approved type listed in accordance with UL 1037 and shall contain keys to gain necessary access

as required by the fire code official.

506.1.1 Locks. An approved lock shall be installed on gates or similar barriers where required by the fire code official .

506.2 Key box maintenance. The operator of the building shall immediately notify the fire code official and provide the new key where a lock is changed or rekeyed. The key to such lock shall be secured in the key box.

Verizon shall contact me for the model of the Knox Box and the padlock.

Disapproved by Falcon Fire Protection District until the items above are corrected.

Please let me know if there are any questions and/or concerns. You may contact me via the email at the top of the letter.

Sincerely,

Curtis L. Kauffman

Curtis L. Kauffman

Fire Prevention Division

Lieutenant/Fire Marshal