# DATE: 5 July 2018

# BUCKSLIP NUMBER: PPR-17-037

# RE:  Development Plan Review – Third Review

# Utility Comments: (gas, electric)

Action Items:

- Provide a separate utility sheet. Show and label existing gas and electric and proposed gas and electric services. Item has been addressed.

- Show and label all applicable easements with width and Reception No. Item has been addressed.

- Ensure that there is at least 3ft of separation between proposed gas and/or electric service lines and any proposed water or wastewater service lines. Item has not been addressed. Appears the minimum separation of 3-feet is not provided between the gas and water on Lot 2. Revise and label separations on both Lots between gas and water.

- Show the proposed location of the gas and electric meters on the elevation plans. Ensure that there is at least 3ft of separation from the gas meter (regulator) and any openings, to include windows and doors. Item has still not been addressed.

Project Specific Information Items:

Contact the Field Engineer for the project area, Tony Colvin, at 719-668-5768 to coordinate gas and electric service prior to construction.

Information Items:

All previous information items still apply.

If you have any questions, please contact Mike Gackle at mgackle@csu.org or 719-668-8262.