PRIVATE DETENTION BASIN /
STORMWATER QUALITY BEST MANAGEMENT PRACTICE
MAINTENANCE AGREEMENT AND EASEMENT

	This PRIVATE DETENTION BASIN / STORMWATER QUALITY BEST MANAGEMENT PRACTICE MAINTENANCE AGREEMENT AND EASEMENT (Agreement) is made by and between EL PASO COUNTY by and through THE BOARD OF COUNTY COMMISSIONERS OF EL PASO COUNTY, COLORADO (Board or County) and Mark Phelan of KESS Properties (Owner or Developer). The above may occasionally be referred to herein singularly as “Party” and collectively as “Parties.”

Recitals
A. WHEREAS, Developer is the owner of certain real estate (the Property or Subdivision) in El Paso County, Colorado, which Property is legally described in Exhibit A attached hereto and incorporated herein by this reference; and

B. WHEREAS, Developer desires to develop the Property for a land use to be known as The Shire at Old Ranch; and

C. WHEREAS, the development of this Property will not substantially increase the volume of water runoff and will improve the quality of the stormwater runoff from the Property, and, therefore, it is in the best interest of public health, safety and welfare for the County to condition approval of this land use on Developer’s promise to construct adequate drainage, water runoff control facilities, and stormwater quality structural Best Management Practices (“BMPs”) for the land use; and

D. WHEREAS, Chapter 8, Section 8.4.5 of the El Paso County Land Development Code, as periodically amended, promulgated pursuant to Section 30-28-133(1), Colorado Revised Statutes (C.R.S.), requires the County to condition approval of all subdivisions/land use on a developer’s promise to so construct adequate drainage, water runoff control facilities, and BMPs in subdivisions; and

E. WHEREAS, the Drainage Criteria Manual, Volume 2, as amended by Appendix I of the El Paso County Engineering Criteria Manual (ECM), as each may be periodically amended, promulgated pursuant to the County’s Colorado Discharge Permit System General Permit (MS4 Permit) as required by Phase II of the National Pollutant Discharge Elimination System (NPDES), which MS4 Permit requires that the County take measures to protect the quality of stormwater from sediment and other contaminants, requires subdividers, developers, landowners, and owners of facilities located in the County’s rights-of-way or easements to provide adequate permanent stormwater quality BMPs with new development or significant redevelopment; and

F. WHEREAS, Section 2.9 of the El Paso County Drainage Criteria Manual provides for a developer’s promise to maintain a subdivision’s drainage facilities in the event the County does not assume such responsibility; and

G. WHEREAS, developers in El Paso County have historically chosen water runoff detention basins as a means to provide adequate drainage and water runoff control in subdivisions, which basins, while effective, are less expensive for developers to construct than other methods of providing drainage and water runoff control; and

H. WHEREAS, Developer desires to construct for the subdivision/land use four (4) detention basin/stormwater quality BMP(s) (“detention basin/BMP(s)”) as the means for providing adequate drainage and stormwater runoff control and to meet requirements of the County’s MS4 Permit, and to operate, clean, maintain and repair such detention basin/BMP(s); and

I. WHEREAS, Developer desires to construct the detention basins/BMP(s) on the property as part of the development plan including Lots 6223000058, 6223000059, 6223000060, 6223000061, as indicated on the development plan, and as set forth on Exhibit B attached hereto; and

J. WHEREAS, Developer shall be charged with the duties of constructing, operating, maintaining and repairing the detention basins/BMP(s) on the Property described in Exhibit B; and

K. WHEREAS, it is the County’s experience that developers and property owners historically have not properly cleaned and otherwise not properly maintained and repaired these detention basins/BMPs, and that these detention basins/BMPs, when not so properly cleaned, maintained, and repaired, threaten the public health, safety and welfare; and

L. WHEREAS, the County, in order to protect the public health, safety and welfare, has historically expended valuable and limited public resources to so properly clean, maintain, and repair these detention basins/BMPs when developers and property owners have failed in their responsibilities, and therefore, the County desires the means to recover its costs incurred in the event the burden falls on the County to so clean, maintain and repair the detention basin/BMP(s) serving this subdivision/land use due to the Developer/Owner’s failure to meet its obligations to do the same; and

M. WHEREAS, the County conditions approval of this land use on the Developer’s promise to so construct the detention basin/BMP(s), and conditions approval on the Owner’s promise to reimburse the County in the event the burden falls upon the County to so clean, maintain and/or repair the detention basins/BMP(s) serving this property; and

N. WHEREAS, the County could condition this land use approval on the Developer’s promise to construct a different and more expensive drainage, water runoff control system and BMPs than those proposed herein, which more expensive system would not create the possibility of the burden of cleaning, maintenance and repair expenses falling on the County; however, the County is willing to forego such right upon the performance of Developer/Owner’s promises contained herein; and

O. WHEREAS, the County, in order to secure performance of the promises contained herein, conditions approval of this land use upon the Developer’s grant herein of a perpetual Easement over a portion of the Property for the purpose of allowing the County to periodically access, inspect, and, when so necessary, to clean, maintain and/or repair the detention basin/BMP(s); and



Agreement
	
NOW, THEREFORE, in consideration of the mutual Promises contained herein, the sufficiency of which are hereby acknowledged, the Parties agree as follows:

1. Incorporation of Recitals:  The Parties incorporate the Recitals above into this Agreement.

2. Covenants Running with the Land: Developer/Owner agrees that this entire Agreement and the performance thereof shall become a covenant running with the land, which land is legally described in Exhibit A attached hereto, and that this entire Agreement and the performance thereof shall be binding upon itself, its successors and assigns.

3. Construction:  Developer shall construct on that portion of the Property described in Exhibit B attached hereto and incorporated herein by this reference, four (4) detention basin/BMP(s). Developer shall not commence construction of the detention basin/BMP(s) until the El Paso County Planning and Community Development Department (PCD) has approved in writing the plans and specifications for the detention basin/BMP(s) and this Agreement has been signed by all Parties and returned to the PCD. Developer shall complete construction of the detention basin/BMP(s) in substantial compliance with the County-approved plans and specifications for the detention basin/BMP(s).  Failure to meet these requirements shall be a material breach of this Agreement, and shall entitle the County to pursue any remedies available to it at law or in equity to enforce the same. Construction of the detention basin/BMP(s) shall be substantially completed within one (1) year (defined as 365 days), which one year period will commence to run on the date the approved plat of this Subdivision is recorded in the records of the El Paso County Clerk and Recorder.  In cases where a subdivision is not required, the one year period will commence to run on the date the Erosion and Stormwater Quality Control Permit (ESQCP) is issued.  Rough grading of the detention basin/BMP(s) must be completed and inspected by the El Paso County Planning and Community Development Department prior to commencing road construction.

In the event construction is not substantially completed within the one (1) year period, then the County may exercise its discretion to complete the project, and shall have the right to seek reimbursement from the Developer/Owner and its successors and assigns, for its actual costs and expenses incurred in the process of completing construction. The term actual costs and expenses shall be liberally construed in favor of the County, and shall include, but shall not be limited to, labor costs, tool and equipment costs, supply costs, and engineering and design costs, regardless of whether the County uses its own personnel, tools, equipment and supplies, etc. to correct the matter. In the event the County initiates any litigation or engages the services of legal counsel in order to enforce the Provisions arising herein, the County shall be entitled to its damages and costs, including reasonable attorney fees, regardless of whether the County contracts with outside legal counsel or utilizes in-house legal counsel for the same. 

4. Maintenance: The Developer/Owner agrees for itself and its successors and assigns, that it will regularly and routinely inspect, clean and maintain the detention basin/BMP(s), and otherwise keep the same in good repair, all at its own cost and expense.  No trees or shrubs that will impair the structural integrity of the detention basin/BMP(s) shall be planted or allowed to grow on the detention basin/BMP(s). 

5. Creation of Easement: Developer/Owner hereby grants the County a non-exclusive perpetual easement upon and across that portion of the Property described in Exhibit B. The purpose of the easement is to allow the County to access, inspect, clean, repair and maintain the detention basin/BMP(s); however, the creation of the easement does not expressly or implicitly impose on the County a duty to so inspect, clean, repair or maintain the detention basin/BMP(s).
6. County’s Rights and Obligations: Any time the County determines, in the sole exercise of its discretion, that the detention basin/BMP(s) is not properly cleaned, maintained and/or otherwise kept in good repair, the County shall give reasonable notice to the Developer/Owner and its successors and assigns, that the detention basin/BMP(s) needs to be cleaned, maintained and/or otherwise repaired. The notice shall provide a reasonable time to correct the problem(s). Should the responsible parties fail to correct the specified problem(s), the County may enter upon the Property to so correct the specified problem(s). Notice shall be effective to the above by the County’s deposit of the same into the regular United States mail, postage pre-paid. Notwithstanding the foregoing, this Agreement does not expressly or implicitly impose on the County a duty to inspect, clean, repair or maintain the detention basin/BMP(s).

7. Reimbursement of County’s Costs / Covenant Running With the Land: The Developer/Owner agrees and covenants, for itself, its successors and assigns, that it will reimburse the County for its costs and expenses incurred in the process of completing construction of, cleaning, maintaining, and/or repairing the detention basin/BMP(s) pursuant to the provisions of this Agreement. 

The term “actual costs and expenses” shall be liberally construed in favor of the County, and shall include, but shall not be limited to, labor costs, tools and equipment costs, supply costs, and engineering and design costs, regardless of whether the County uses its own personnel, tools, equipment and supplies, etc. to correct the matter. In the event the County initiates any litigation or engages the services of legal counsel in order to enforce the provisions arising herein, the County shall be entitled to its damages and costs, including reasonable attorney’s fees, regardless of whether the County contracts with outside legal counsel or utilizes in-house legal counsel for the same. 

8. Contingencies of Land Use/Land Disturbance Approval: Developer/Owner’s execution of this Agreement is a condition of land use/land disturbance approval. 

The County shall have the right, in the sole exercise of its discretion, to approve or disapprove any documentation submitted to it under the conditions of this Paragraph, including but not limited to, any separate agreement or amendment, if applicable, identifying any specific maintenance responsibilities not addressed herein. The County’s rejection of any documentation submitted hereunder shall mean that the appropriate condition of this Agreement has not been fulfilled.

9. Agreement Monitored by El Paso County Planning and Community Development Department and/or El Paso County Department of Public Works:  Any and all actions and decisions to be made hereunder by the County shall be made by the Director of the El Paso County Planning and Community Development Department and/or the Director of the El Paso County Department of Public Works. Accordingly, any and all documents, submissions, plan approvals, inspections, etc. shall be submitted to and shall be made by the Director of the Planning and Community Development Department and/or the Director of the El Paso County Department of Public Works.

10. Indemnification and Hold Harmless: To the extent authorized by law, Developer/Owner agrees, for itself, its successors and assigns, that it will indemnify, defend, and hold the County harmless from any and all loss, costs, damage, injury, liability, claim, lien, demand, action and causes of action whatsoever, whether at law or in equity, arising from or related to its intentional or negligent acts, errors or omissions or that of its agents, officers, servants, employees, invitees and licensees in the construction, operation, inspection, cleaning (including analyzing and disposing of any solid or hazardous wastes as defined by State and/or Federal environmental laws and regulations), maintenance, and repair of the detention basin/BMP(s), and such obligation arising under this Paragraph shall be joint and several. Nothing in this Paragraph shall be deemed to waive or otherwise limit the defense available to the County pursuant to the Colorado Governmental Immunity Act, Sections 24-10-101, et seq. C.R.S., or as otherwise provided by law. 

11. Severability:  In the event any Court of competent jurisdiction declares any part of this Agreement to be unenforceable, such declaration shall not affect the enforceability of the remaining parts of this Agreement.

12. Third Parties: This Agreement does not and shall not be deemed to confer upon or grant to any third party any right to claim damages or to bring any lawsuit, action or other proceeding against either the County, the Developer/Owner, or their respective successors and assigns, because of any breach hereof or because of any terms, covenants, agreements or conditions contained herein.

13. Solid Waste or Hazardous Materials:  Should any refuse from the detention basin/BMP(s) be suspected or identified as solid waste or petroleum products, hazardous substances or hazardous materials (collectively referred to herein as “hazardous materials”), the Developer/Owner shall take all necessary and proper steps to characterize the solid waste or hazardous materials and properly dispose of it in accordance with applicable State and/or Federal environmental laws and regulations, including, but not limited to, the following: Solid Wastes Disposal Sites and Facilities Acts, §§ 30-20-100.5 – 30-20- 119, C.R.S., Colorado Regulations Pertaining to Solid Waste Disposal Sites and Facilities, 6 C.C.R. 1007-2, et seq., Solid Waste Disposal Act, 42 U.S.C. §§ 6901-6992k, and Federal Solid Waste Regulations 40 CFR Ch. I. The County shall not be responsible or liable for identifying, characterizing, cleaning up, or disposing of such solid waste or hazardous materials. Notwithstanding the previous sentence, should any refuse cleaned up and disposed of by the County be determined to be solid waste or hazardous materials, the Developer/Owner, but not the County, shall be responsible and liable as the owner, generator, and/or transporter of said solid waste or hazardous materials.

14. Applicable Law and Venue:  The laws, rules, and regulations of the State of Colorado and El Paso County shall be applicable in the enforcement, interpretation, and execution of this Agreement, except that Federal law may be applicable regarding solid waste or hazardous materials. Venue shall be in the El Paso County District Court.
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Exhibit A

A PARCEL OF LAND LOCATED IN THE SW1/4 OF THE SW1/4 OF SEC. 23 T. 12 S., R. 69 W. OF THE 6TH P.M., EL PASO COUNTY, COLORADO   

	Address
	Zoning
	Legal Description
	Parcel Number
	Reception Number

	3820 Old Ranch Rd.
	RR-5
	W 315 FT OF S2S2SW4 EX RDS SEC 23-12-66
	6223000061
	216003121

	3890 Old Ranch Rd.
	RR-5
	E 385 FT OF W 715 FT OF S2S2SW4 EX S 30 FT SEC 23-12-66 19
	6223000060
	216003167

	10655 Howells Rd.
	RR-5
	TRACT IN SW4SW4 SEC 23-12-66 AS FOLS, BEG ON W LN OF SD SW4 AT PT 660 FT N FROM SW COR THEREOF, TH N ON W LN 322.5 FT, E AT R/A 715 FT, S AT R/A 322.5 FT, TH W 715 FT TO POB EX W 30 FT
	6223000059
	216003151

	10755 Howells Rd.
	RR-5
	TRACT IN SW4SW4 SEC 23-12-66 AS FOLS, BEG ON W LN OF SD SW4 AT PT 982.5 FT N FROM SW COR THEREOF, TH N ON W LN 322.5 FT, E AT R/A 715 FT, S AT R/A 322.5 FT, TH W 715 FT TO POB EX W 30 FT
	6223000058
	213027769
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Standard Operation Procedures for [image: ]
Inspection and Maintenance of 
Extended Detention Basin(s) The Shire at Old Ranch 

Owners:

	Mark Phelan
4955 Austin Bluffs Parkway
Colorado Springs, CO, 80918

	Monica Phelan
10755 Howells Rd. 
Colorado Springs, CO, 80908










El Paso County Department of Public Works 
3275 Akers Drive 
Colorado Springs, CO 80922 
dotweb@elpasoco.com 
719-520-6900

Introduction 
This plan addresses operation and maintenance of public detention / water quality facilities (per Drainage Plan) constructed as part of The Shire at Old Ranch development project at the northeast corner of Howells Rd and Old Ranch Rd. (EPC PCD projects number(s): PPR2410). The Legal Description of the property is attached. 
Background 
The State of Colorado Department of Public Health and Environment, Water Quality Control  Division (CDPHE), has implemented federal regulations within the State of Colorado through  permitting, and has included El Paso County as one of numerous Municipal Separate Storm Sewer  Systems (MS4s) required to be permitted in compliance with National Pollutant Discharge  Elimination System (NPDES) Phase 2 Regulations, as defined within Colorado’s Phase 2 Municipal  Guidance.  
NPDES Phase 2 MS4s stormwater discharges are covered under a general permit under the  Colorado Discharge Permit System (CDPS) under Regulation 61, and as a minimum require the  MS4’s operator (e.g., El Paso County) to develop, implement, and enforce a stormwater  management program to reduce the discharge of pollutants to the maximum extent practicable to  protect water quality requirements of the Colorado Water Quality Control Act, Colorado Code of  Regulations [CCR] 61.8(11)(a)(i)). 
This Stormwater Facilities Operation and Maintenance Plan (O&M Plan) is for public subregional  detention facilities (per Drainage Plan) constructed as part of the development  project referenced above.
Associated Agreements 
There are no associated agreements.
Funding for an Organization of Facility Operation and Maintenance 
Mark Phelan will be responsible for operations and maintenance of all of the detention facilities located on The Shire at Old Ranch upon acceptance of the facilities. 
Site and Facilities Description 
Refer to The Shire at Old Ranch Drainage Plan for specifications and locations of detention facilities.  
Extended Detention Basin (EDB) Description 
The subsections below describe general EDB operations and maintenance.  
EDB-1 GENERAL EDB CONCEPT 
Extended Detention Basins (EDBs) are one of the most common types of permanent stormwater  control measures utilized within the Front Range of Colorado. An EDB is a sedimentation basin  designed to “extend” the runoff detention time, but to drain completely sometime after  stormwater runoff ends. An EDB’s drain time for the water quality portion of the facility is typically  40 hours. The basins are considered to be “dry” because the majority of the basin is designed  not to have a significant permanent pool of water remaining between runoff events. 
EDBs are an adaptation of a detention basin used for flood control, with the primary difference  being the addition of forebays, micropools and a slow release outlet design. Forebays are  shallow concrete “pans” located at the inflow points to the basin and are provided to facilitate  sediment removal within a contained area prior to releasing into the pond. The forebays collect  and briefly hold stormwater runoff resulting in a process called sedimentation, dropping sediment  out of the stormwater. The stormwater is then routed from the forebay into the concrete trickle  channel and upper basin, the large grassy portion of the basin. The EDB includes an outlet  structure that extends the drain time of frequently occurring runoff events to facilitate pollutant  removal. An EDB also includes a small micropool just upstream of the outlet structure or built  into the outlet structure. The micropool is designed to hold a small amount of water to keep  sediment and floatables from blocking the outlet orifices. 
EDB-2 INSPECTING EXTENDED DETENTION BASINS (EDBs) 
EDB-2.1 Access and Easements 
Inspection and maintenance personnel may utilize the attached stormwater facility map  containing the location(s) of the access points and maintenance easements of the EDB(s) within  this development. 
EDB-2.2 Stormwater Management Facilities Locations 
Inspection and maintenance personnel may utilize the attached stormwater facility map containing the location(s) of the EDB(s) within this development. 
EDB-2.3 Extended Detention Basin (EDB) Features 
EDBs have a number of features that are designed to serve a particular function. Many times the  proper function of one feature depends on another. For example, if a forebay is not properly  maintained, it could negatively affect the performance of a downstream feature (trickle channel,  micropool, etc.). 
Therefore, it is critical that each feature of the EDB is properly inspected and maintained to  ensure that the overall facility functions as it was intended. Below is a list and description of the  most common features within an EDB and the corresponding maintenance inspection items that  can be anticipated:

Table EDB-1: Typical Inspection & Maintenance Requirements Matrix 
	EDB Features 
	Sediment  Removal
	Mowing/  Weed  
Control
	Trash &  
Debris  
Removal
	Erosion
	Over 
grown  
Vegetation  
Removal
	Standing  
Water  
(mosquito/  algae  
control)
	Structure  Repair

	Inflow Points  (outfalls) 
	X 
	
	X 
	X 
	
	
	X

	Forebays 
	X 
	
	X 
	
	
	
	X

	Low-Flow  
Channel 
	X 
	
	X 
	X 
	X 
	
	X

	Bottom Stage 
	X 
	X 
	X 
	X 
	X 
	X
	

	Micropool 
	X 
	
	X 
	
	X 
	X 
	X

	Outlet Works 
	X 
	
	X 
	
	
	
	X

	Emergency  
Spillway 
	
	
	X 
	X 
	X 
	
	X

	Upper Stage 
	
	
	X 
	X
	
	
	

	Embankment 
	
	X 
	
	X 
	X
	
	



EDB-2.3.1 Inflow Points 
Inflow Points or Outfalls into EDBs are the point source of the stormwater discharge into  the facility. An inflow point is commonly a storm sewer pipe with a flared end section that  discharges into the EDB. In some instances, an inflow point could be a drainage channel  or ditch that flows into the facility. 
An energy dissipater (riprap or hard armor protection) is typically immediately downstream  of the discharge point into the EDB to protect from erosion. In some cases, the storm sewer  outfall can have a toe- wall or cut-off wall immediately below the structure to prevent  undercutting of the outfall from erosion. 
The typical maintenance items that are found with inflow points are as follows: 
a. Riprap Displaced – Many times, because of repeated impact/force of water, the  riprap can shift and settle. If any portion of the riprap apron appears to have settled,  soil is present between the riprap, or the riprap has shifted, maintenance may be  required to ensure future erosion is prevented. 
b. Erosion Present/Outfall Undercut – In some situations, the energy dissipater may  not have been sized, constructed, or maintained appropriately and erosion has  occurred. Any erosion within the vicinity of the inflow point will require maintenance  to prevent damage to the structure(s) and sediment transport within the facility. 
c. Sediment Accumulation – Because of the turbulence in the water created by the  energy dissipater, sediment often deposits immediately downstream of the inflow  point. To prevent a loss in hydraulic performance of the upstream infrastructure,  sediment that accumulates in this area must be removed in a timely manner. 
d. Structural Damage – Structural damage can occur at any time during the life of  the facility. Typically, for an inflow, the structural damage occurs to the pipe flared  end section (concrete or steel). Structural damage can lead to additional operating  problems with the facility, including loss of hydraulic performance. 
e. Woody Growth/Weeds Present – Undesirable vegetation can grow in and around the inflow area to an EDB that can significantly affect the performance of the  drainage facilities discharging into the facility. This type of vegetation includes trees  (typically cottonwoods) and dense areas of shrubs (willows). If woody vegetation is  not routinely mowed/removed, the growth can cause debris/sediment to  accumulate, resulting in blockage of the discharge. Also, tree roots can cause  damage to the structural components of the inflow. Routine maintenance is  essential for trees (removing a small tree/sapling is much cheaper and “quieter”  than a mature tree). In addition, noxious weeds growing in the facility can result in  the loss of desirable native vegetation and impact adjacent open spaces/land. 
EDB-2.3.2 Forebay 
A forebay is a solid surface (pad), typically constructed of concrete, immediately  downstream of the inflow point. The forebay is designed to capture larger particles and  trash to prevent them from entering the main portion of the EDB. The solid surface is  designed to facilitate mechanical sediment removal (via a skid steer or shovel). The  forebay typically includes a small diameter discharge pipe or weir on the downstream end, which is designed to drain the forebay in a specified period of time to promote  sedimentation. Forebays vary in size and depth depending on the design and site  constraints. 
The typical maintenance items that are found with forebays are as follows: 
a. Sediment/Debris Accumulation – Because this feature of the EDB is designed  to provide the initial sedimentation, debris and sediment frequently accumulate in  this area. If the sediment and debris is not removed from the forebay on a regular  basis, it can significantly affect the function of other features within the EDB. Routine  sediment removal from the forebay can significantly reduce the need for dredging  of the main portion of the EDB using specialized equipment (long reach  excavators). Routine removal of sediment from the forebay can substantially decrease the long-term sediment removal costs of an EDB. 
b. Concrete Cracking/Failing – The forebay is primarily constructed of concrete,  which cracks, spalls, and settles. Damage to the forebay can result in deceased  performance and impact maintenance efforts. 
c. Drain Pipe/Weir Clogged – Many times the drainpipe or weir can be clogged  with debris, and prevent the forebay from draining properly. If standing water is  present in the forebay (and there is not a base flow), the forebay is most likely not  draining properly. This can result in a decrease in performance and create potential  nuisances with stagnant water (mosquitoes). 
d. Weir/Drain Pipe Damaged – Routine maintenance activities, vandalism, or age  may cause the weir or drain pipe in the forebay to become damaged. Weirs are  typically constructed of concrete, which cracks and spalls. The drainpipe is typically  constructed with plastic, which can fracture.

EDB-2.3.3 Trickle Channel (Low-Flow) 
The trickle channel conveys stormwater from the forebay to the micro- pool of the EDB.  The trickle channel is typically made of concrete. 
However, grass lined (riprap sides protected) is also common and can provide for an  additional means of water quality within the EDB. The trickle channel is typically 6-9 inches  in depth and can vary in width. 
The typical maintenance items that are found with trickle channels are as follows: 
a. Sediment/Debris Accumulation – Trickle channels are typically designed with a  relatively flat slope that can promote sedimentation and the collection of debris.  Also, if a trickle channel is grass lined it can accumulate sediment and debris at a  much quicker rate. Routine removal of accumulated sediment and debris is  essential in preventing flows from circumventing the trickle channel and affecting  the dry storage portion of the pond. 
b. Concrete/Riprap Damage – Concrete can crack, spall, and settle and must be  repaired to ensure proper function of the trickle channel. Riprap can also shift over  time and must be replaced/repaired as necessary. 
c. Woody Growth/Weeds Present – Because of the constant moisture in the area  surrounding the trickle channel, woody growth (cottonwoods/willows) can become  a problem. Trees and dense shrub type vegetation can affect the capacity of the  trickle channel and can allow flows to circumvent the feature. 
d. Erosion Outside of Channel – In larger precipitation events, the trickle channel  capacity will likely be exceeded. This can result in erosion immediately adjacent to  the trickle channel and must be repaired to prevent further damage to the structural  components of the EDB. 
EDB-2.3.4 Bottom Stage (Initial Surcharge) 
The bottom stage is at least 4 inches deeper than the upper stage and is located directly  in front of the outlet works structure, and typically above the permanent water surface of  the micropool and the invert of the trickle channel. The bottom stage is designed to store  the smaller runoff events, assists in keeping the majority of the basin bottom dry resulting  in easier maintenance operations, and enhances the facility’s pollutant removal  capabilities. This area of the EDB may develop wetland vegetation. 
The typical maintenance items that are found with the bottom stage are as follows: 
a. Sediment/Debris Accumulation – The micropool can frequently accumulate  sediment and debris. This material must be removed to maintain pond volume and  proper function of the outlet structure. 
b. Woody Growth/Weeds Present – Because of the constant moisture in the soil  surrounding the micropool, woody growth (cottonwoods/willows) can create  operational problems for the EDB. If woody vegetation is not routinely  mowed/removed, the growth can cause debris/sediment to accumulate outside of  the micropool, which can cause problems with other EDB features. Also, tree roots  can cause damage to the structural components of the outlet works. Routine  management is essential for trees (removing a small tree/sapling is much cheaper  and less disruptive than removing a mature tree). 
c. Bank Erosion – The micropool is usually a couple feet deeper than the other  areas of the ponds. Erosion can be caused by water dropping into the micropool if 
adequate protection/armor is not present. Erosion in this area must be mitigated to  prevent sediment transport and other EDB feature damage. 
d. Mosquitoes/Algae Treatment – Nuisance created by stagnant water can result  from improper maintenance/treatment of the micropool. Mosquito larvae can be laid  by adult mosquitoes within the permanent pool. Also, aquatic vegetation that grows  in shallow pools of water can decompose causing foul odors. Chemical/mechanical  treatment of the micropool may be necessary to reduce these impacts to adjacent  homeowners. 
e. Petroleum/Chemical Sheen – Many indicators of illicit discharges into the storm  sewer systems will be present in the micropool area of the EDB. These indicators  can include sheens, odors, discolored soil, and dead vegetation. If it is suspected  that an illicit discharge has occurred, contact County Stormwater immediately.  Proper removal/mitigation of contaminated soils and water in the EDB is necessary  to minimize any environmental impacts downstream. 
EDB-2.3.5 Micropool 
The micropool is a concrete or grouted boulder walled structure directly in front of the outlet  works. At a minimum, the micropool is 2.5 feet deep and is designed to hold water. The  micropool is critical in the proper function of the EDB; it allows suspended sediment to be  deposited at the bottom of the micropool and prevents these sediments from being  deposited in front of the outlet works causing clogging of the outlet structure, which results  in marshy areas within the top and bottom stages. 
The typical maintenance items that are found with micropools are as follows: 
a. Sediment/Debris Accumulation – The micropool can frequently accumulate  sediment and debris. This material must be removed to maintain pond volume and  proper function of the outlet structure. 
b. Woody Growth/Weeds Present – Because of the constant moisture in the soil  surrounding the micropool, woody growth (cottonwoods/willows) can create  operational problems for the EDB. If woody vegetation is not routinely  mowed/removed, the growth can cause debris/sediment to accumulate outside of  the micropool, which can cause problems with other EDB features. Also, tree roots  can cause damage to the structural components of the outlet works. Routine  management is essential for trees (removing a small tree/sapling is much cheaper  and less disruptive than removing a mature tree). 
c. Mosquitoes/Algae Treatment – Nuisance created by stagnant water can result  from improper maintenance/treatment of the micropool. Mosquito larvae can be laid  by adult mosquitoes within the permanent pool. Also, aquatic vegetation that grows  in shallow pools of water can decompose causing foul odors. Chemical/mechanical  treatment of the micropool may be necessary to reduce these impacts to adjacent  homeowners. 
d. Petroleum/Chemical Sheen – Many indicators of illicit discharges into the storm  sewer systems will be present in the micropool area of the EDB. These indicators  can include sheens, odors, discolored soil, and dead vegetation. If it is suspected  that an illicit discharge has occurred, contact the supervisor immediately. Proper  removal of contaminated soils and water in the EDB is necessary to minimize any  environmental impacts downstream.

EDB-2.3.6 Outlet Works 
The outlet works is the feature that drains the EDB in specified release rates and periods  of time. The outlet works is typically constructed of reinforced concrete into the  embankment of the EDB. The concrete structure typically has steel orifice plates  anchored/embedded into it to control stormwater release rates. The larger openings for  flood control on the outlet structure typically have trash racks over them to prevent  clogging. The water quality orifice plate with small diameter holes will typically have a well  screen covering it to prevent smaller materials from clogging it. The outlet structure is the  single-most important feature in the EDB operation. Proper inspection and maintenance  of the outlet works is essential in ensuring the long-term operation of the EDB. 
The typical maintenance items that are found with the outlet works are as follows: 
a. Trash Rack/Well Screen Clogged – Floatable material that enters the EDB will  most likely make its way to the outlet structure. This material is trapped against the  trash racks and well screens on the outlet structure (which is why they are there).  This material must be removed on a routine basis to ensure the outlet structure  drains in the specified design period. 
b. Structural Damage – The outlet structure is primarily constructed of concrete,  which can crack, spall, and settle. The steel trash racks and well screens are also  susceptible to damage. 
c. Orifice Plate Missing/Not Secure – Many times residents, property owners, or  maintenance personnel will remove or loosen orifice plates if they believe the pond  is not draining properly. Any modification to the orifice plate(s) will significantly affect  the designed discharge rates for water quality and/or flood control. Modification of  the orifice plates is not allowed without EPC approval. 
d. Manhole Access – Access to the outlet structure is necessary to properly  inspect and maintain the facility. If access is difficult or not available to inspect the  structure, chances are it will be difficult to maintain as well. 
e. Woody Growth/Weeds Present – Because of the constant moisture in the soil  surrounding the outlet works, woody growth (cottonwoods/willows) can create  operational problems for the EDB. If woody vegetation is not routinely  mowed/removed, the growth can cause debris/sediment to accumulate around the  outlet works, which can cause problems with other EDB features. Also, tree roots  can cause damage to the structural components of the outlet works. Routine  management is essential for trees (removing a small tree/sapling is much cheaper  and less disruptive than removing a mature tree). 
EDB-2.3.7 Emergency Spillway 
An emergency spillway is typical of all EDBs and designed to serve as the overflow in the  event the volume of the pond is exceeded. The emergency spillway is typically armored  with riprap (or other hard armor) and is sometimes buried with soil. The emergency  spillway is typically a weir (notch) in the pond embankment. Proper function of the  emergency spillway is essential to ensure flooding does not affect adjacent properties. 
The typical maintenance items that are found with emergency spillways are as follows: 
a. Riprap Displaced – As mentioned before, the emergency spillway is typically  armored with riprap to provide erosion protection. Over the life of an EDB, the riprap  may shift or dislodge due to flow.
b. Erosion Present – Although the spillway is typically armored, stormwater  flowing through the spillway can cause erosion damage. Erosion must be repaired  to ensure the integrity of the basin embankment, and proper function of the spillway. 
c. Woody Growth/Weeds Present – Management of woody vegetation is  essential in the proper long-term function of the spillway. Larger trees or dense  shrubs can capture larger debris entering the EDB and reduce the capacity of the spillway. 
d. Obstruction Debris – The spillway must be cleared of any obstruction (man made or natural) to ensure the proper design capacity. 
EDB-2.3.8 Upper Stage (Dry Storage) 
The upper stage of the EDB provides the majority of the water quality flood detention  volume. This area of the EDB is higher than the micro- pool and typically stays dry, except  during storm events. The upper stage is the largest feature/area of the basin. Sometimes,  the upper stage can be utilized for park space and other uses in larger EDBs. 
With proper maintenance of the micropool and forebay(s), the upper stage should not  experience much sedimentation; however, bottom elevations should be monitored to  ensure adequate volume. 
The typical maintenance items that are found with upper stages are as follows: 
a. Vegetation Sparse – The upper basin is the most visible part of the EDB, and  therefore aesthetics is important. Adequate and properly maintained vegetation can  greatly increase the overall appearance and acceptance of the EDB by the public.  In addition, vegetation can reduce the potential for erosion and subsequent  sediment transport to the other areas of the pond. 
b. Woody Growth/Undesirable Vegetation – Although some trees and woody  vegetation may be acceptable in the upper basin, some thinning of cottonwoods  and willows may be necessary. Remember, the basin will have to be dredged to  ensure volume, and large trees and shrubs will be difficult to protect during that 
operation. 
c. Standing Water/Boggy Areas – Standing water or boggy areas in the upper  stage is typically a sign that some other feature in the pond is not functioning  properly. Routine maintenance (mowing, trash removal, etc.) can be extremely  difficult for the upper stage if the ground is saturated. If this inspection item is  checked, make sure you have identified the root cause of the problem. 
d. Sediment Accumulation – Although other features within the EDB are designed  to capture sediment, the upper storage area will collect sediment over time.  Excessive amounts of sedimentation will result in loss of storage volume. It may be difficult to determine if this area has accumulated sediment without a field survey. 
Below is a list of indicators: 
1. Ground adjacent to the trickle channel appears to be several inches higher  than concrete/riprap 
2. Standing water or boggy areas in upper stage 
3. Uneven grades or mounds 
4. Micropool or Forebay has excessive amounts of sediment
e. Erosion (banks and bottom) – The bottom grades of the dry storage are  typically flat enough that erosion should not occur. However, inadequate vegetative  cover may result in erosion of the upper stage. Erosion that occurs in the upper  stage can result in increased dredging/maintenance of the micropool. 
f. Trash/Debris – Trash and debris can accumulate in the upper area after events, or from illegal dumping. This material can accumulate and clog  the EDB outlet works. 
g. Maintenance Access – Most EDBs typically have a gravel/concrete  maintenance access path to either the upper stage, outlet works, and/or forebay.  This access path should be inspected to ensure the surface is still drivable. Some  of the smaller EDBs may not have maintenance access paths; however, the  inspector should verify that access is available from adjacent properties. 
EDB-2.3.9 Miscellaneous 
There are a variety of inspection/maintenance issues that may not be attributed to a single  feature within the EDB. This category on the inspection form is for maintenance items that  are commonly found in the EDB but may not be attributed to an individual feature. 
a. Encroachment in Easement Area – Private lots/property can sometimes be  located very close to the EDBs, even though they are required to be located in tracts  with drainage easements. Property owners may place landscaping, trash, fencing,  etc. within easement areas that may affect maintenance or operation of the facility. 
b. Graffiti/Vandalism – Damage to the EDB infrastructure can be caused by  vandals. If criminal mischief is evident, the inspector should forward this information  to the local Sheriff’s Office. 
c. Public Hazards – Public hazards include items such as vertical drops of greater  than 4-feet, containers of unknown/suspicious substances, exposed metal/jagged  concrete on structures. If any hazard is found within the facility area that poses an  immediate threat to public safety, contact the Sheriff at 911 immediately! 
d. Burrowing Animals/Pests – Prairie dogs and other burrowing rodents may  cause damage to the EDB features and negatively affect the vegetation within the  EDB. Consult EPC Environmental Division if this becomes an issue. 
e. Other – Any miscellaneous items not on the form should be entered here. 
EDB-3 MAINTAINING EXTENDED DETENTION BASINS (EDBS) 
EDB-3.1 Maintenance Personnel 
Maintenance personnel must be qualified to properly maintain EDBs. Inadequately trained  personnel can cause additional problems resulting in additional maintenance costs. 
EDB-3.2 Equipment 
It is imperative that the appropriate equipment and tools are taken to the field with the operations  crew. The types of equipment/tools will vary depending on the task at hand. Below is a list of  tools, equipment, and material(s) that may be necessary to perform maintenance on an EDB: 
1.) Loppers/Tree Trimming Tools  
2.) Mowing Tractors
3.) Trimmers (extra string)  
4.) Shovels 
5.) Rakes 
6.) All Surface Vehicle (ASVs)  
7.) Skid Steer 
8.) Backhoe 
9.) Track Hoe/Long Reach Excavator  
10.) Dump Truck 
11.) Jet-Vac Machine 
12.) Engineers Level (laser)  
13.) Riprap (Minimum - Type M)  
14.) Filter Fabric 
15.) Erosion Control Blanket(s)  
16.) Seed Mix (Native)  
17.) Illicit Discharge Cleanup Kits  
18.) Trash Bags 
19.) Tools (wrenches, screw drivers, hammers, etc.)  
20.) Chain Saw 
21.) Confined Space Entry Equipment 
22.) Approved Stormwater Facility Operation and Maintenance Manual 
Some items identified above may not be needed for every maintenance operation.  However, this equipment should be available to the maintenance operations crews should the  need arise. 
EDB-3.3 Safety 
Vertical drops may be encountered in areas located within and around the facility. Avoid walking  on top of retaining walls or other structures that have a significant vertical drop. If a vertical drop  is identified within the EDB that is greater than 48” in height, make the appropriate note/comment  on the maintenance inspection form. 


EDB-3.4 Maintenance Categories and Activities 
A typical EDB Maintenance Program will consist of three broad categories of work: routine,  minor, and major maintenance activities. Within each category of work, a variety of maintenance  activities can be performed on an EDB. A maintenance activity can be specific to each feature  within the EDB, or general to the overall facility. A variety of maintenance activities are typical of  EDBs. The maintenance activities range in magnitude from routine trash pickup to the  reconstruction of drainage infrastructure. The following three sub-sections (3.5, 3.6, and 3.7)  explain each of the categories and briefly describe the typical maintenance activities for an  EDB, including the objectives and frequency of actions. 
EDB-3.5 Routine Maintenance Activities 
The majority of this work consists of regularly scheduled mowing and trash and debris pickups  for stormwater management facilities during the growing season. This includes items such as  the removal of debris/material that may be clogging the outlet structure well screens and trash  racks. It also includes activities such as weed control, mosquito treatment, and algae treatment.  These activities will normally be performed numerous times during the year. These items can be  completed without any prior correspondence with the EPC Stormwater; however, completed inspection and maintenance forms shall be retained for each inspection and maintenance  activity. 
The Maintenance Activities are summarized below, and further described in the following sub sections. 
TABLE – EDB-2 Summary of Routine Maintenance Activities 
	MAINTENANCE  ACTIVITY 
	MINIMUM FREQUENCY 
	LOOK FOR 
	MAINTENANCE ACTION

	
	
	
	

	Mowing 
	Twice annually 
	Excessive grass  
height/aesthetics 
	Mow grass to a height of 4” to 6”

	Trash/Debris  
Removal 
	Twice annually 
	Trash & debris in EDB 
	Remove and dispose of trash and  debris

	Outlet Works  
Cleaning
	As needed – after  
significant rain events – twice annually at a  
minimum
	Clogged outlet  
structure; ponding  
water
	Remove and dispose of  
debris/trash/sediment to allow outlet  to function properly

	Weed control 
	Minimum twice annually 
	Noxious weeds;  
Unwanted vegetation
	Treat w/ herbicide or hand pull;  Consult the local weed specialist

	Mosquito  
Treatment 
	As needed 
	Standing water/ 
mosquito habitat 
	Treat w/ EPA approved chemicals

	Algae Treatment 
	As needed 
	Standing water/ Algal  growth/green color 
	Treat w/ EPA approved chemicals




EDB-3.5.1 Mowing 
Occasional mowing is necessary to limit unwanted vegetation and to improve the overall  appearance of the EDB. Native vegetation should be mowed to a height of 4-to-6 inches  tall. Grass clippings should be collected and disposed of properly. 
Frequency – Routine - Minimum of twice annually or depending on aesthetics. 
EDB-3.5.2 Trash/Debris Removal 
Trash and debris must be removed from the entire EDB area to minimize outlet clogging  and to improve aesthetics. This activity must be performed prior to mowing operations. 
Frequency – Routine – Prior to mowing operations and minimum of twice annually. 
EDB-3.5.3 Outlet Works Cleaning 
Debris and other materials can clog the outlet work’s well screen, orifice plate(s), and trash  rack. This activity must be performed anytime other maintenance activities are conducted  to ensure proper operation. 
Frequency - Routine – After significant rainfall event or concurrently with other  maintenance activities. 
EDB-3.5.4 Weed Control 
Noxious weeds and other unwanted vegetation must be treated as needed throughout the  EDB. This activity can be performed either through mechanical means (mowing/pulling) or  with herbicide. Consultation with the Environmental Division at 719-520-7878 is highly  recommended prior to the use of herbicide.
Frequency – Routine – As needed based on inspections. 
EDB-3.5.5 Mosquito/Algae Treatment 
Treatment of permanent pools is necessary to control mosquitoes and undesirable aquatic  vegetation that can create nuisances. Only EPA approved chemicals/materials can be  used in areas that are warranted. 
Frequency – As needed. 
EDB- 3.6 Minor Maintenance Activities 
This work consists of a variety of isolated or small-scale maintenance or operational problems.  Most of this work can be completed by a small crew, tools, and small equipment. These items  may require prior correspondence with EPC Stormwater and require completed inspection and  maintenance forms to be submitted to EPC upon request for each inspection and maintenance  activity. 
Table – EDB-3 Summary of Minor Maintenance Activities 
	MAINTENANCE  ACTIVITY 
	MINIMUM FREQUENCY 
	LOOK FOR 
	MAINTENANCE ACTION

	
	
	
	

	Sediment  
Removal
	As needed; typically  every 1–2 years
	Sediment build-up;  
decrease in pond 
volume
	Remove and dispose of sediment

	Erosion Repair 
	As needed, based upon  inspection
	Rills/gullies forming on  side slopes, trickle  
channel, other areas
	Repair eroded areas Revegetate;  address source of erosion

	Vegetation  
Removal/Tree  
Thinning
	As needed, based upon inspection
	Large trees/wood  
vegetation in lower stage  of pond
	Remove vegetation; restore  grade and surface

	Drain  
Cleaning/Jet Vac
	As needed,based upon  inspection
	Sediment build-up/ non  draining system 
	Clean drains; Jet Vac if needed




EDB-3.6.1 Sediment Removal 
Sediment removal is necessary to maintain the original design volume of the EDB and to  ensure proper function of the infrastructure. Regular sediment removal (minor) from the  forebay, inflow(s), and trickle channel can significantly reduce the frequency of major  sediment removal activities (dredging) in the upper and lower stages. The minor sediment  removal activities can typically be addressed with shovels and smaller equipment. Major  sediment removal activities will require larger and more specialized equipment. The major  sediment activities will also require surveying with an engineer’s level, and consultation  with EPC Stormwater Staff to ensure design volumes/grades are achieved. 
Stormwater sediments removed from EDBs do not meet the criteria of “hazardous waste”.  However, these sediments are contaminated with a wide array of organic and inorganic  pollutants and handling must be done with care. Sediments from permanent pools must  be carefully removed to minimize turbidity, further sedimentation, or other adverse water  quality impacts. Sediments should be transported by motor vehicle only after they are  dewatered. All sediments must be taken to a landfill for proper disposal. Prompt and  thorough cleanup is important should a spill occur during transportation. 
Frequency – Nonroutine – As necessary based upon inspections. Sediment removal in the forebay and trickle channel may be necessary as frequently as every 1-2 years. 
EDB-3.6.2 Erosion Repair 
The repair of eroded areas is necessary to ensure the proper function of the EDB, minimize  sediment transport, and to reduce potential impacts to other features. Erosion can vary in  magnitude from minor repairs to trickle channels, energy dissipaters, and rilling to major  gullies in the embankments and spillways. The repair of eroded areas may require the use  of excavators, earthmoving equipment, riprap, concrete, erosion control blankets, and turf  reinforcement mats. Major erosion repair to the pond embankments, spillways, and  adjacent to structures will require consultation with EPC Stormwater Staff. 
Frequency – Nonroutine – As necessary based upon inspections. 
EDB-3.6.3 Vegetation Removal/Tree Thinning 
Dense stands of woody vegetation (willows, shrubs, etc) or trees can create maintenance  problems for the infrastructure within an EDB. Tree roots can damage structures and  invade pipes/channels thereby blocking flows. Also, trees growing in the upper and lower  stages of the EDB will most likely have to be removed when sediment/dredging operations  occur. A small tree is easier to remove than a large tree, therefore, regular  removal/thinning is preferred. All trees and woody vegetation that is growing in the bottom  of the EDB or near structures (inflows, trickle channels, outlet works, emergency spillways,  etc) should be removed. Any trees or woody vegetation in the EDB should be limited to  the upper portions of the pond banks. 
Frequency – Nonroutine – As necessary based upon inspections. 
EDB-3.6.4 Clearing Drains/Jet-Vac 
An EDB contains many structures, openings, and pipes that can be frequently clogged  with debris. These blockages can result in a decrease of hydraulic capacity and create  standing water in areas outside of the micropool. Often the blockage to this infrastructure  can be difficult to access and/or clean. Specialized equipment (jet-vac machines) may be  necessary to clear debris from these difficult areas. 
Frequency – Nonroutine – As necessary based upon inspections. 
EDB-3.7 Major Maintenance Activities 
This work consists of larger maintenance/operational problems and failures within the  stormwater management facilities. All of this work requires consultation with EPC Stormwater  Staff to ensure the proper maintenance is performed. This work requires that the staff review the  original design and construction drawings to assess the situation and assign the necessary  maintenance. An ESQCP permit may be required for major maintenance activities. This  work may also require more specialized maintenance equipment, design/details, surveying, or  assistance through private contractors and consultants.

Table – EDB-4 Summary of Major Maintenance Activities 
	MAINTENANCE  ACTIVITY 
	MINIMUM FREQUENCY 
	LOOK FOR 
	MAINTENANCE ACTION

	
	
	
	

	Major Sediment  Removal
	As needed – based upon  scheduled inspections
	Large quantities of sediment;  reduced pond capacity
	Remove and dispose of  sediment. Repair vegetation  as needed

	Major Erosion  
Repair
	As needed – based upon  scheduled inspections
	Severe erosion including  gullies, excessive soil 
displacement, areas of  
settlement, holes
	Repair erosion – find cause  of problem and address to  avoid future erosion

	Structural Repair 
	As needed – based upon  scheduled inspections
	Deterioration and/or damage  to structural components – broken concrete, damaged  pipes, outlet works
	Structural repair to restore  the structure to its original  design




EDB-3.7.1 Major Sediment Removal 
Major sediment removal consists of removal of large quantities of sediment or removal of  sediment from vegetated areas. Care shall be given when removing large quantities of  sediment and sediment deposited in vegetated areas. Large quantities of sediment need  to be carefully removed, transported and disposed of. Vegetated areas need special care  to ensure design volumes and grades are preserved. 
Frequency – Nonroutine – Repair as needed based upon inspections. 
EDB-3.7.2 Major Erosion Repair 
Major erosion repair consists of filling and revegetating areas of severe erosion.  Determining the cause of the erosion as well as correcting the condition that caused the  erosion should also be part of the erosion repair. Care should be given to ensure design  grades and volumes are preserved. 
Frequency – Nonroutine – Repair as needed based upon inspections. 
EDB-3.7.3 Structural Repair 
An EDB includes a variety of structures that can deteriorate or be damaged during the  course of routine maintenance. These structures are constructed of steel and concrete  that can degrade or be damaged and may need to be repaired or re-constructed from time  to time. 
These structures include items like outlet works, trickle channels, forebays, inflows, and  other features. In-house operations staff can perform some of the minor structural repairs.  Major repairs to structures may require input from a structural engineer and specialized  contractors. Consultation with EPC Stormwater Staff should take place prior to all  structural repairs. 
Frequency – Nonroutine – Repair as needed based upon inspections. 
Reference: 
This manual is adapted from SEMSWA and the Town of Parker, Colorado, STORMWATER  PERMANENT BEST MANAGEMENT PRACTICES (PBMP) LONG-TERM OPERATION AND  MAINTENANCE MANUAL, October 2004
For additional resources and contact info, visit the EPC Stormwater website: 
https://publicworks.elpasoco.com/stormwater/ 
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Notary Public

Executed this day of 20 by:

BOARD OF COUNTY COMMISSIONERS
OF EL PASO COUNTY, COLORADO

By: Christina Prete, Stormwater Operations & Compliance Manager
Engineering Division, Department of Public Works
Designee of Joshua Palmer, County Engineer
Authorized signatory pursuant to Resolution No. 24-145

The foregoing instrument was acknowledged before me this day of 20,
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Witness my hand and official seal.
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Approved as to Content and Form:

Assistant County Attorney
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