FALCON FIRE PROTECTION DISTRICT

Fire Prevention Division

7030 Old Meridian Road

Falcon, Colorado 80831

Business Number: 719-495-4050     Business Fax: 719-495-3112

Lieutenant/Fire Marshal	             Curtis L. Kauffman

Email: ckauffman@falconfirepd.org                     Cell #: 719-641-2139

Date: June 4, 20266

To: EDARP

C/O: Joe Letke

Planning & Community Development

2882 International Circle, Suite 110

Colorado Springs, CO 80910

Phone: 719-520-7964

Email: joeletke@elpasoco.com

Project Name: 13635 Murphy Road-Accessory Living Quarters for Permanent Occupancy Special Use

File Prefix: AL-Special Use

Parcel/s: 4205003008

Zone: RR-5

File Number: AL2615

This letter serves as comments for the special use. You are responsible for complying with all sections, codes and references with the fire code based on the 2021 International Fire Code.

PLEASE READ THIS ENTIRE DOCUMENT, YOU ARE RESPONSIBLE FOR EVERYTHING CONTAINED HERIN!

The following are ACTION ITEMS that need to be completed.

503.1 Where required. Fire apparatus access roads shall be provided and maintained in accordance with Sections 503.1.1 through 503.1.3 and Appendix D.

503.1.1 Buildings and facilities. Approved fire apparatus access roads shall be provided for

every facility, building or portion of a building hereafter constructed or moved into or within the jurisdiction. The fire apparatus access road shall comply with the requirements of this section and shall extend to within 150 feet (45 720 mm) of all portions of the facility and all portions of the exterior walls of the first story of the building as measured by an approved route around the exterior of the building or facility.

Exceptions:

1. The fire code official is authorized to increase the dimension of 150 feet (45 720

mm) where any of the following conditions occur:

1.1. The building is equipped throughout with an approved automatic sprinkler

system installed in accordance with Section 903.3.1.1, 903.3.1.2 or 903.3.1.3.

1.2. Fire apparatus access roads cannot be installed because of location on

property, topography, waterways, nonnegotiable grades or other similar

conditions, and an approved alternative means of fire protection is provided.

1.3. There are not more than two Group R-3 or Group U occupancies.

2. Where approved by the fire code official, fire apparatus access roads shall be

permitted to be exempted or modified for solar photovoltaic power generation

facilities.

503.2 Specifications. Fire apparatus access roads shall be installed and arranged in accordance with Sections 503.2.1 through 503.2.8 and Appendix D.

503.2.1 Dimensions. Fire apparatus access roads shall have an unobstructed width of not less than 20 feet (6096 mm), exclusive of shoulders, except for approved security gates in accordance with Section 503.6, and an unobstructed vertical clearance of not less than 13 feet 6 inches (4115 mm). modifications to the required access widths where they are inadequate for fire or rescue operations or where necessary to meet the public safety objectives of the jurisdiction.

503.2.2 Authority. The fire code official shall have the authority to require or permit modifications to the required access widths where they are inadequate for fire or rescue operations or where necessary to meet the public safety objectives of the jurisdiction.

Section 503.2.3 Surface. Fire apparatus access roads shall be designed and maintained to support the imposed loads of fire apparatus and shall be surfaced so as to provide all-weather driving capabilities.

503.2.4 Turning radius. The required turning radius of a fire apparatus access road shall be determined by the fire code official. 33’ inside and 53’ outside radius. Resubmit the site plan showing the turning radius and travel of a fire apparatus.

503.2.5 Dead ends. Dead-end fire apparatus access roads in excess of 150 feet in length shall be provided with an approved area for turning around fire apparatus. The driveway is more than 150’ in length, one bump-out shall be proved at the 550-foot to 600-foot point along the existing driveway from Murphy Road.

503.2.7 Grade. The grade of the fire apparatus access road shall be within the limits established by the fire code official based on the fire department’s apparatus. 10% maximum.

503.2.8 Angles of approach and departure. The angles of approach and departure for fire apparatus access roads shall be within the limits established by the fire code official based on the fire department’s apparatus. Less than 8° degrees (not % percent).

Section 505.1. Address Identification. New and existing buildings shall have approved address numbers, building numbers or approved building identification placed in a position that is plainly legible and visible from the street or road fronting the property. These numbers shall contrast with their background. Address numbers shall be Arabic numbers or alphabetical letters. Numbers shall be a minimum of five (5) inches (127 mm) high with a minimum stroke width of one half (0.5) inch (12.7 mm). Where access is by means of a private road and the building cannot be viewed from the public way, a monument, pole or other means of signage shall be used to identify the structure.” Address numbers shall be visible from the street side and in both directions of road travel and on the new home.

Section D102.1 Access and loading. Amend Section D102.1 to read as follows:

D102.1 Access and loading. Facilities, buildings, or portions of buildings hereafter constructed shall be accessible to fire department apparatus by way of an approved fire apparatus access road with asphalt, concrete, or other approved driving surface capable of supporting the imposed load of fire apparatus weighing up to 75,000 pounds with a minimum single axle weight of 27,000 pounds. Alternative methods such as brick pavers, road, base, and gravel as approved by the fire code official.

D105.1 Where required. Where the vertical distance between the grade plane and the highest roof surface exceeds 30 feet (9144 mm), approved aerial fire apparatus access roads shall be provided. For purposes of this section, the highest roof surface shall be determined by measurement to the eave of a pitched roof, the intersection of the roof to the exterior wall, or the top of parapet walls, whichever is greater.

Exception: Where approved by the fire code official, buildings of Type IA, Type IB or Type IIA construction equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 and having fire fighter access through an enclosed stairway with a Class I standpipe from the lowest level of fire department vehicle access to all roof surfaces.

D105.2 Width. Aerial fire apparatus access roads shall have a minimum unobstructed width of 26 feet (7925 mm), exclusive of shoulders, in the immediate vicinity of the building or portion thereof.

D105.3 Proximity to building. One or more of the required access routes meeting this condition shall be located not less than 15 feet (4572 mm) and not greater than 30 feet (9144 mm) from the building and shall be positioned parallel to one entire side of the building. The side of the building on which the aerial fire apparatus access road is positioned shall be approved by the fire code official.

D105.4 Obstructions. Overhead utility and power lines shall not be located over the aerial fire apparatus access road or between the aerial fire apparatus road and the building. Other obstructions shall be permitted to be placed with the approval of the fire code

official.

The following are ATTENTION ITEMS that apply to this review.

Section 1402.1 Temporary Fire Access Road. Temporary access roads shall be an all-weather surface comprised of either the first lift of asphalt or concrete/compacted gravel to a thickness capable of supporting the imposed loads of fire department apparatus. A 20-foot minimum width shall be maintained unless the permanent road is designed less than 20 feet, in which case the temporary road shall be the intended width of the permanent road. Adequate street signs and fire lane signs shall be installed where applicable. Temporary access roads must be maintained in accordance with this section. Temporary roads serving as fire lanes shall not be in place more than 6 months without special approval from the fire department.”

TIMING OF INSTALLATION: Fire department access roads shall be made serviceable prior to and during the time of construction except when approved alternative methods of protection are provided.

ACCESS FOR FIREFIGHTING: Approved vehicle access for firefighting shall be provided to all construction/demolition sites. Vehicle access shall be provided by either temporary or permanent roads capable of supporting vehicle loading under all weather conditions. Vehicle access shall be maintained until permanent fire apparatus access roads are available.

Attention Contractor/Applicant:

YOU ARE RESPONSIBLE TO COMPLETE THE FOLLOWING ITEMS.

Please complete the following items:

- Permits – Ensure all applicable permits are obtained from the Pikes Peak Regional Building Department (PPRBD).

- Follow the Colorado State Forest Service for all mitigation guidelines for the new structure; csfs.colostate.edu.

- Show the proposed site for the new ALQ, the bump-out along the existing driveway, and vehicle tracking on an updated site plan for approval.

- I encourage an early assistance meeting be conducted prior to construction to discuss the length of the driveway (no fees).

- Review of the comment letter from Falcon Fire Protection District. You are responsible for complying with the entire fire code as amended and any applicable NFPA’s referenced.

- Ensure all Action Items have been addressed.

- Plan review comments (this letter) shall be on site and available to the fire inspector.

Please let me know if there are any questions and/or concerns. You may contact me via email at the top of the letter.

Sincerely,

Curtis L. Kauffman

Curtis L. Kauffman

Fire Prevention Division

Lieutenant/Fire Marshal