Project: Father & Sons Distillery – Storage Facility

Location: 22420 Business Park, Mayberry Business Park, El Paso County

Applicant: Father & Sons Distillery – Lot 1, Mayberry Filing No. 4

Consultant: Live Edge Consulting

Fire District: Ellicott Fire Protection District (EFPD)

The proposed Father & Sons Distillery Storage Facility includes the phased construction of four 100’ x 100’ storage buildings intended to store barrels of whisky utilizing internal cross-style aisles, beginning in 2026 and assumed to conclude in 2029. Due to existing roadway constraints along Highway 94, EFPD identifies extended Aggregate Response Times (ART) ranging from 8–9 minutes during early phases of development, exceeding the district’s goal for an ART by 1–2 minutes.

To mitigate this risk, the project incorporates enhanced fire protection features, including automatic fire sprinkler systems, fire department connections (FDCs), dual interior hose valves, and expanded fire apparatus access exceeding minimum IFC requirements. While current access limitations increase response time, future roadway improvements associated with the Mayberry Housing Development are anticipated to reduce ART by 2–3 minutes once Mayberry Drive connects to North Log Road.

Based on the proposed fire protection systems, operational accommodations, phased construction controls, and conditions of approval outlined herein, the project can achieve an acceptable level of fire and life safety consistent with the 2015 International Fire Code, subject to EFPD oversight and continued coordination during all phases of development. The Conditions of Approval noted below are intended to be for Lot 1 Mayberry Colorado Springs Filing No. 4

Conditions of Approval – Fire Protection & Access

- Fire Department Access & Aggregate Response Time

  - Fire department access shall be maintained in a manner that minimizes ART and ensures continuous access for emergency apparatus throughout all phases of construction and occupancy.

    - IFC §503.1 – Fire apparatus access roads required

    - IFC §503.2 – Specifications

  - Any future roadway connections (including Mayberry Drive connection to Positive Place and connection to North Log Road) shall not restrict existing approved fire department access routes and shall be coordinated with Ellicott Fire Protection District (EFPD) prior to implementation.

    - IFC §104.11 – Alternative materials and methods

    - IFC §503.4 – Obstruction of fire apparatus access roads

- Fire Apparatus Access Roads / Fire Lanes

  - Fire apparatus access roads shall have an unobstructed width of not less than 20 feet, exclusive of parking, and shall be approved by EFPD.

    - IFC §503.2.1 – Dimensions

  - Fire Apparatus Access – Loading Dock Area – Load-Bearing Surface Clarification:

    - On the proposed Site Development Plan, the paved area located south of the loading dock is designed at a minimum width of 16 feet. The developer proposes to supplement this paved section with a mountable curb and reinforced rock landscaping system constructed over a compacted crushed gravel base specifically engineered to support the imposed loads of fire department apparatus.

    - The reinforced surface shall be designed and constructed to accommodate a minimum fire apparatus live load of not less than 75,000 pounds, consistent with IFC fire apparatus access road performance expectations, without rutting, displacement, or structural failure. When combined, the paved surface and reinforced load-bearing landscaping area will provide a continuous, unobstructed fire apparatus access width ranging from a minimum of 25 feet up to 30 feet, thereby exceeding the 2015 IFC minimum required unobstructed width of 20 feet.

    - The site developer shall coordinate with the EFPD as the AHJ to finalize and approve the landscaping and reinforcement design, including load capacity verification, surface stability, and year-round accessibility, to ensure safe and reliable fire department operations.

  - Fire Lane Materials Approval and Verification:

    - The proposed combination fire lane consisting of paved surface and reinforced rock landscaping with a compacted crushed gravel base is permitted, subject to verification that the system is capable of supporting required fire apparatus loads. Verification shall include certification demonstrating compliance with fire apparatus loading requirements as determined by the EFPD. Written approval of the fire lane materials and design shall be issued by EFPD prior to final inspection and shall be a condition of issuance of the Certificate of Occupancy (CO).

      - IFC §503.2.3 – Surface

      - IFC §503.2.7 – Grade

      - IFC §104.11 – Alternative materials and methods

  - Fire lanes shall be maintained free of obstructions at all times.

    - IFC §503.4 – Obstruction

- Fire Hydrant & Fire Department Connection (FDC)

  - Fire hydrants shall be located and maintained in accordance with EFPD standards and shall provide unobstructed access to the Fire Department Connection (FDC).

    - IFC §507.5.1 – Where required

    - IFC §507.5.4 – Obstruction

  - The Fire Department Connection shall be located and configured as approved by EFPD and remain unobstructed at all times.

    - IFC §912.2 – Location

    - IFC §912.3 – Access

- Storage Facility Design & Commodity Arrangement

  - Storage buildings housing distilled spirits shall comply with the applicable High-Piled Storage and flammable/combustible liquid storage provisions of the IFC.

    - IFC §3201.1 – Scope

    - IFC Chapter 50 – Hazardous materials

  - Aisle widths and layout shall remain consistent with approved plans to allow firefighter access and fire attack operations.

    - IFC §3206 – Aisle dimensions

  - Any increase in storage height, barrel count, or commodity classification shall require resubmittal and approval by EFPD.

    - IFC §105.6 – Required permits

- Fire Protection Systems & Hose Valves

  - The automatic fire sprinkler system shall be installed and maintained in accordance with NFPA 13, as adopted by the IFC.

    - IFC §903.3.1.1 – NFPA 13

  - Two hose valves shall be installed—one at the north entrance and one at the south entrance—as requested by EFPD to support interior fire attack operations.

    - IFC §905.3 – Class I standpipe systems

    - IFC §905.4 – Location of Class I standpipe hose connections

  - The fire sprinkler system and hose valves shall be capable of simultaneous operation when supplied by a fire department pumper connected to the FDC.

    - IFC §912.1 – Installation

- Phased Construction (2026– and beyond)

  - Each phase of construction shall be independently compliant with fire and life safety requirements prior to occupancy.

    - IFC §102.1 – General

  - Fire department access, hydrants, fire lanes, and fire protection systems shall be installed and approved prior to combustible storage in each phase.

    - IFC §503.1.1 – Buildings exceeding 30 feet

    - IFC §507.5.1 – Where required

  - A final inspection and approval by EFPD shall be required for each phase prior to use.

    - IFC §109.1 – Inspections

- Authority Having Jurisdiction (AHJ)

  - The Ellicott Fire Protection District is the Authority Having Jurisdiction (AHJ) for fire and life safety matters and retains the authority to require additional measures deemed necessary to ensure firefighter safety and effective emergency response.

    - IFC §104.1 – General authority

    - IFC §104.8 – Modifications

  - Failure to comply with these conditions may result in delayed approvals, restricted use, or enforcement action as permitted by the IFC.

    - IFC §109.3 – Violation penalties

Approval of this development is contingent upon strict adherence to these conditions to ensure safe fire department access, effective emergency operations, and firefighter safety throughout all phases of construction and occupancy.